## Slide 1
Corrosion Control Module

## Slide 2: Project Partners
Hazen and Sawyer
Carollo
Santa Clara Valley Water District
LA Sanitation District
Gwinnett County (GA)
El Paso Water Utilities
UFTREEO (University of Florida)
Sacramento State
University of Arizona-WEST Center
TrojanUV
Xylem Inc.
Process Applications Inc.

## Slide 3: Expected Learning Outcomes
Learners will be able to…
  Explain the importance of corrosion control in drinking water
  Explain potential corrosion outcomes from unstable water quality
  Identify key water quality parameters that impact corrosion
  Identify water quality targets to avoid corrosion
  Describe methods to test water stabilization before introduction into a distribution system
  Describe stabilization methods for water treated by high-pressure membranes
  Discuss potential impacts from blending different water qualities in a distribution system

## Slide 4: Module Outline
The role of corrosion control in drinking water and potable reuse
How corrosion control works
Health implications and regulations
Case Study: Flint, MI Lead Crisis
Technical discussion of corrosion control
Process operations: Operator responsibility in maintaining corrosion control programs
Testing, operation, monitoring, and maintenance priorities for corrosion control
Critical monitoring and response procedure
Safety considerations

## Slide 5: Role in Potable Reuse

## Slide 6: Corrosion Control Important for Safe Drinking Water
Water that is not properly stabilized can result in metals such as lead and copper entering water supply at unsafe levels
Use of reverse osmosis in potable reuse in particular requires re-stabilization following removal of hardness and alkalinity from the water
All new water supplies entering a distribution system must be considered in terms of their impact on corrosion and stability management

## Slide 7: Process Overview and Introduction
Role of corrosion control in drinking water and potable reuse
What corrosion control is and how it works
Process-specific considerations

## Slide 8: Drinking Water Distributions Contain Different Pipe Materials from Water Mains to Premise Plumbing (i.e., In Homes/Buildings)
Copper Pipe
Common in household plumbing
New pipe surfaces have strong potential for copper leaching
Cement Mortar-Lined Ductile Iron Pipe
Reflective of water corrosivity toward cement, asbestos cement, and concrete pipe surfaces
New CML pipe is most susceptible to corrosive water
Unlined Cast Iron Pipe
Tuberculated, old unlined cast iron pipe is often responsible for colored water and decreased chlorine residual
May be sensitive to change in flow direction, pressure swings, and water chemistry
Lead Components
Lead solder was common in older homes for joining copper pipe lengths; also in brass fixtures
Lead service lines in older distribution systems increase risk

## Slide 9: Distribution Systems Are Assets to be Maintained But Also Are Potential Sources of Contamination
Water entering drinking water distribution systems has the potential to corrode pipes leading to
  Colored/dirty water complaints
  Premature pipe breakage
  Pinhole leaks in building and home plumbing systems
  Health impacts from lead and copper leaching: e.g., Flint, MI and Washington, DC
http://flintwaterstudy.org/about-page/about-us/

## Slide 10: Corrosion Control Requires Holistic Distribution System Management
Corrosion
Lead and Copper Release
Water Loss and Leaks
Water Quality Optimization
Asset Management
Simultaneous Compliance
Customer Relations
Notes: Increasingly difficult to find the right balance to achieve WQ goals and simultaneous compliance while minimizing corrosivity to multiple distribution system materials. Understanding corrosion in the distribution system is central to implementing holistic distribution system management of all of these factors. In fact, as part of the expert panel for the project, a common theme among the experts was that distribution system optimization can be used to increase the effectiveness of corrosion control and can be a proactive alternative to CCT upgrades. Achieve consistent disinfectant residual and pH, as fluctuating water quality tends to cause more corrosion. This can be achieving by flushing, main cleaning and renewal, storage facility enhancement, microbial control such as nitrification, hydraulic modeling.

## Slide 11: Holistic View
Corrosion in water systems is a function of raw water quality, treatment, and distribution system operations…. A true “source-to-tap” approach is needed to ensure optimum corrosion control treatment (OCCT).
To achieve OCCT overall process control and distribution system water quality optimization must also be achieved
OCCT is not an independent, separate process

## Slide 12: Primary Water Quality Parameters that Impact Iron-Based Materials
pH
Calcium
Disin-fectant
Alka-linity
Dis-solved Oxygen
Notes: pH:
Ferric iron precipitates on pipes are less likely to dissolve into water at higher pH if water is sufficiently oxic
pH, Alk, Ca:
Calcium carbonate precipitation potential (CCPP) index provides an indication of calcium carbonate saturation
DO and Disinfectant:
On balance:
Anoxic conditions can promote ferric conversion to ferrous iron, which is more soluble
Oxidant can minimize iron dissolution

## Slide 13: Primary Water Quality Parameters that Impact Cement-Based Materials
pH
Calcium
Alka-linity
Notes: Calcium carbonate precipitation potential (CCPP) index provides an indication of calcium carbonate saturation

## Slide 14: Primary Water Quality Parameters that Impact Copper Materials
Alkalinity
Chloride
pH
Sulfate
Disinfect-ant
Dissolved Oxygen
Notes: Alkalinity and pH are strongest influence
pH:
Copper corrosion decreases with increasing pH
Alk:
Copper corrosion increases with increasing alkalinity
Optimal is a balance of positive CCPP without excessive alkalinity.
Higher anions can also increase corrosion, as can an increase in DO. However, release of copper to the water (rather than corrosion and buildup of deposits) can increase with stagnant conditions.

## Slide 15: Primary Water Quality Parameters that Impact Lead Materials
pH
Calcium
Alkalinity
Sulfate
Chloride
Dissolved Oxygen
Notes: Solder
pH:
Leaching is less at pH 8 – 8.5.
Alk and Ca:
Passivating film can limit solubility of lead compounds
Impact of other factors requires testing
Brass
Brass is comprised primarily of copper and zinc, and historically up to about 6% lead

## Slide 16: Health Impacts and Regulations

## Slide 17: The Lead and Copper Rule (LCR): Developed to Protect Sensitive Populations
Promulgated in 1991
Requires systems to monitor drinking water at customer taps
  All community water systems
  Non-transient non-community water systems
Established action levels
  Action level for Pb = 0.015 mg/L
  Action level for Cu =1.3 mg/L
Also requires systems to provide individual Pb tap results to people who receive water from sites that were sampled.
Notes: Community Water System (CWS): A public water system that supplies water to the same population year-round. Non-Transient Non-Community Water System (NTNCWS): A public water system that regularly supplies water to at least 25 of the same people at least six months per year, but not year-round. Some examples are schools, factories, office buildings, and hospitals which have their own water systems.

## Slide 18: Health Concerns: Lead
Cumulative toxin – distributed to brain, liver, kidneys, bones
  Children especially susceptible
Delay in physical and mental development in children
  W.H.O. estimates 600,000 new cases/year of intellectual disabilities
  50% from SE Asia, 40% from Wester Pacific and Eastern Mediterranean
No level is considered “Safe”

## Slide 19: Sources of Lead Come from Distribution System Materials
Locations of lead in the Flint Water System (City of Flint Oct. Quarterly Water Quality Report, https://www.cityofflint.com/wp-content/uploads/Quarterly-Water-Quality-Report_Oct-15.pdf)

## Slide 20: A Portion of CDC’s Lead Infographic
https://www.cdc.gov/nceh/lead/infographic.htm

## Slide 21: Health Concerns: Copper
Micronutrient for humans
  Acute poisoning (usually occupational exposure) results in gastrointestinal distress
Chronic exposure at high concentration damages liver and kidneys
Major target of LCR Regulation: Protection of individuals with Wilson’s Disease
  Copper builds up in liver over time and causes later-onset liver toxicity

## Slide 22: LCR Regulation Timeline: Rules are Evolving and Must be Tracked by Operations and Management
LCR promulgated
EPA publishes set of proposed minor revisions
EPA publishes LCRMR based on proposed revisions in 1996
EPA begins National Review of LCR
EPA releases DWLRP
Short-term revisions & clarifications
Long-term revisions
1991
1996
2000
2004
2005
2007
2017
Reduction of Lead in DW Act of 2011
Notes: In 2011, the Reduction of Lead in Drinking Water Act was signed. This changed the definition of “lead-free” under SDWA by reducing the lead content from 8% to a weighted average of not more than 0.25% of the wetted surface material. The 2007 revisions were meant to prevent an event like what happened in DC from ever happening again. Unfortunately, the crisis in Flint happened anyway…

## Slide 23: Case Study: Flint Water Crisis

## Slide 24: 2013 and 2014: Economic Hardship Leads to Alternative Water Supply Considerations
Historically, Flint was a wholesale customer of Detroit Water and Sewerage District (DWSD), but considering alternatives
  Flint water treatment plant only for “emergency operation”
  In 2006, studies indicate Flint River water can be safely treated but it does not have enough capacity for permanenent use
In 2013, the Karengodi Water Authority (KWA) created to provide water from Lake Huron to Flint WTP, but pipeline won’t be ready for years
  City Council Approved 7 – 1, Emergency Manager Ed Kurtz
  DWSD provides notice of termination, effective 1 year later
  June 2013 – Flint decides to use Flint River as Interim water supply
April 2014, Flint began operation of their water treatment plant with the Flint River as the source
‘13
‘06
‘14
‘67

## Slide 25: City of Flint Water Treatment Plant

## Slide 26: City of Flint Water Treatment Plant: Ignored Non-Functioning Processes, Added Raw Water Chlorine, and Replaced GAC with Anthracite/Sand Filters
“Advanced Treatment” included ozone, lime softening, GAC filters
Not Working
Anthracite over Sand
Active Intermediate Cl2
Raw Cl2 ?
Notes: Note the importance of not taking shortcuts in process maintenance and intended purpose: i.e., GAC was not simply a filter media, but was meant to help control DBPs.

## Slide 27: Numerous Water Quality Issues Occurred Post-Conversion
August and September 2014: Boil Water Alerts after high coliform bacteria and E. coli detected at taps throughout the City
Summer 2014: Increase in reported cases of Legionnaire’s
Trend goes unnoticed
October 2014: GM discontinues use of Flint water, citing “too corrosive”
July – December 2014: Round 1 LCR sampling (90th %’ile = 6ppb)
January 2015: Operational Evaluation required for DBPs
  “Two quarters of samples taken indicate that future violations are inevitable for total THM without some modifications to the water system”
January – June 2015: Round 2 LCR sampling (90th %’ile = 11ppb)
August 2015: A second Operational Evaluation required for DBPs
  “Six quarters of sampled taken have resulted in annual average violations for tTHM”
Summer 2015, More Cases of Legionnaire’s.
Almost immediately after conversion, Flint began experiencing serious water quality issues
‘14
‘15

## Slide 28: Michigan DEQ Took Two Rounds of LCR Samples in 2014/2015
Flint and DEQ did not have an accurate inventory of lead service lines
2 Data Points were removed from the analysis
Data came back above the 15 ppb action level (AL)
Excluded because home had whole-house filter
Excluded because location was a business
Notes: Because of the way the rule was written, regulators failed to note that lead contamination was occurring in the distribution system. By eliminated two outlier samples, the data came back showing that fewer than 10% of sampling sites exceeded the action level.

## Slide 29: But Something Wasn’t Right
In February 2015, a concerned citizen requested the City measure lead in her home
  Lead measured at 104ppb and 397ppb (15ppb AL)
  Iron exceeded detection capabilities
Tested child’s blood lead levels
  Increased from 2ug/dL  6.5 ug/dL
  (above 5ug/dL triggers public health response)
DEQ suggested indoor plumbing corrosion
A concerned citizen starts the ball rolling

## Slide 30: Contact with EPA
Citizen brought concerns to the City, and they sent her to the EPA.
Miguel Del Toral from the regional office reviewed the data
  “Didn’t understand how the lead in her water could be so high when the City was using corrosion control”
Del Toral contacted Marc Edwards from Virginia Tech, and documented his concerns

## Slide 31: Initial Sampling by Edwards Confirmed Elevated Lead Levels in the Home (Note Target Lead Concentration Should Have Been <15 ppb)
Del Toral, 2015

## Slide 32: Expanded testing in Flint by Edwards Group Confirmed Elevated Lead Levels

## Slide 33: Independently, Research on Children’s Lead Levels Showed Disturbing Trends
Elevated lead after switching water sources

## Slide 34: What Happened? Water Chemistry in Flint Was Corrosive and Had No Corrosion Control in Place
Parameter | Flint1 | Detroit2
Chloride (mg/L) | 74 - 87 | 4.2 - 40
Hardness (mg/L) | 168 – 210 | 90 – 120
Alkalinity (mg/L) | 60 – 115 | 69 – 78
TOC (mg/L) | 2.6 | N/A
Cl2 (DS) (mg/L) | 0.2 – 2.8 | 0.5 – 1.01
THM/HAA5 (mg/L) | 94/24 | 33.6/11.3
pH | 7.4 – 8.53 | 6.9 – 8.0
1Flint data based upon December, 2014 Water Quality Summary
2Detroit data from 2014 Detroit Water and Sewerage
3Analysis of subsequent MORs indicated pH reduced significantly throughout 2015, from an average of 9.1 in December 2014 to an average of 7.3 in August 2015.
From: Chemical & Engineering News, 2016, Volume 94, Issue 7, http://cen.acs.org/articles/94/i7/Lead-Ended-Flints-Tap-Water.html%20

## Slide 35: Key Take Away Messages from Flint
Events underscore need to manage water chemistry, especially when bringing in new supplies
Proper corrosion control can prevent public health impacts and aesthetic concerns
Evaluation of new water supplies and blended water supplies should occur PRIOR to conversion
  Recommend pipe loop studies and coupon studies
Proper management AND communication could have prevented this situation

## Slide 36: Technical Discussion of Corrosion Control

## Slide 37: Multiple Biological and Chemical Processes Control Distribution System Behavior
Particles
http://www.biofilm.montana.edu/multimedia/images/index.html

## Slide 38: Optimum Corrosion Control Treatment (OCCT)
Defined as…
  “the corrosion control treatment that minimizes the lead and copper concentrations at users' taps while insuring that the treatment does not cause the water system to violate any national primary drinking water regulations.”
Much more than simply adjusting pH or adding phosphate
Maintaining existing pipe scales are key
Metal solubility is important factor

## Slide 39: Types of Scale on Lead (Pb) Pipe
Simple carbonate or hydroxycarbonate Pb(II) mineral
Simple Pb(II) orthophosphate mineral
Simple PbO2 solid phase, by itself or mixed with Pb(II) phases
Mix of Pb(II) phases
Protective “diffusion barrier” materials
  Could be insoluble amorphous Pb(II) phase
  Adherent non-Pb phase
Surface fouling deposit
  Primarily not made of lead, usually not crystalline
  Lead may sorb to surface
Michael Schock: Simultaneous Compliance: Myth versus Reality

## Slide 40: Scale Analysis – Existing NYC Lead Pipe
Photograph of interior of NYC distribution system pipe showing a very
thin brown surface layer with a thick white layer beneath

## Slide 41: Lead Scale Analysis Reveals Multiple Types of Deposits
Lead Pipe
L2
L1
Plattnerite – PbO2 and Pyromorphite – Pb5Cl(PO4)3
Hydrocerussite - Pb3(CO3)2(OH)2 and some Pyromorphite - Pb5Cl(PO4)3
Two distinct layers: L1 – a thin grey/brown scale
L2 – a thick white scale
When water chemistry changes, lead scale may change form, resulting in release of lead into drinking water

## Slide 42: Multiple Water Quality Factors Affect Metal Release and Must be Controlled – 1
Temperature
pH & stability (buffering)
ORP/corrosion potential
Type and amount of disinfectant
Dissolved oxygen
Alkalinity/DIC
Iron (deposition and corrosion)
Calcium
Manganese
Aluminum
NOM (type, amount)
Amount of mixing of WTPs or sources
Notes: Note that many factors in water chemistry can impact lead solubility. The take-away is that ANY changes made at a treatment plant should be carefully evaluated for potential implication on lead and copper. For DPR, diurnal changes in ammonia, sulfide, sulfate, chloride, DO, should also be considered.

## Slide 43: Multiple Water Quality Factors Affect Metal Release and Must be Controlled – 2
Orthophosphate
Polyphosphate (amount and type)
Chloride
Sulfate
Sorptive surfaces downstream of LSLs (ie. galvanized interior pipe)
Ammonia
Hydrogen Sulfide
Silica
Microbial activity (nitrification and other)
Notes: Note that many factors in water chemistry can impact lead solubility. The take-away is that ANY changes made at a treatment plant should be carefully evaluated for potential implication on lead and copper. For DPR, diurnal changes in ammonia, sulfide, sulfate, chloride, DO, should also be considered.

## Slide 44: Upstream Treatment Can Also Affect Lead Release in the Distribution System – 1
Iron or manganese post-precipitation
Alum carry-over
Anion exchange for U, As, NOM, etc.
Sequestration of Fe, Ca, Mg, Mn by polyphosphate or blended phosphate
Change in amount or type of disinfectant
Oxidation/filtration for Fe or Mn removal
Optimum or enhanced coagulation
  Changes in type of coagulant
  Changes in coagulant dosage
Notes: Again, many other process changes at the drinking water plant (or advanced purification plant for DPR) have the potential to change lead/copper release. Changes should NOT be made without evaluation of unintended consequences.

## Slide 45: Upstream Treatment Can Also Affect Lead Release in the Distribution System – 2
Aeration
Season water quality changes: pH, alkalinity, chloride, sulfate, NOM, temperature
GAC for DBP control
Ammonia oxidation
Tight membrane (RO or NF)
Relining/replacement of mains (chemical changes or physical disturbances)
Notes: Again, many other process changes at the drinking water plant (or advanced purification plant for DPR) have the potential to change lead/copper release. Changes should NOT be made without evaluation of unintended consequences.

## Slide 46: Chemical Changes Cause Dissolution of PbO2 into Water
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
–.8
–.6
–.4
–.2
.2
.4
.6
.8
1.0
pH
Eh (volts)
Pb
++
Pb(OH)42-
PbCO3°
Pb(CO3)22-
--
Pb3(CO3)2(OH)2 (s)
Pb metal
PbO2 (plattnerite)
DIC = 18 mg C/L
Pb = 0.010 mg/L
1.2
0.0
-1.0
Drop in pH at surface from treatment change, blend ratio, reactions, nitrification, etc. results in soluble lead release
Drop in ORP from treatment change or DS oxidant demand
Disinfectant demand in DS must be controlled and enough free chlorine consistently maintained throughout distribution
Michael Schock: Simultaneous Compliance: Myth versus Reality
Notes: Chemical changes can move one way or another

## Slide 47: pH Fluctuation Controlled by Buffer Capacity
Figure 2.3 from EPA OCCT Manual (Buffer Intensity as a Function of pH at Different DIC Values (Clement and Schock, 1998b, Figure 1)
High alkalinity (“dissolved inorganic carbon” or DIC) requires significant amount of acid or base to adjust pH
As a plus, higher buffer capacity minimizes likelihood of changes in pH in distribution system
Notes: highest buffer intensity at a pH of approximately 6.3 and minimum intensity at pH
values between 8.0 and 8.5. Thus, waters with pH between 8 and 8.5 and low DIC (less than
about 10 mg/L as C) have low buffer intensity and may have more variable pH within the
distribution system, whereas waters outside this pH range will have higher buffer intensity and
may exhibit less variability in pH levels in the distribution system. Increasing DIC in waters with
pH values in the 8 – 8.5 range will not result in appreciable increases in buffer intensity.
Additional buffer intensity may result when phosphate or silicate chemicals are dosed at a high
concentration relative to DIC.

## Slide 48: The Challenge for DPR Operations Teams
Manage water quality goals to ensure optimal range of pH, alkalinity, corrosion control inhibitor addition, etc. are maintained
Use RTW to track changes in stability indices such as LSI and CCPP
Ensure diurnal and seasonal water quality changes in source water do not negatively impact corrosion control strategy
Track water chemistry daily to ensure OCCT is maintained

## Slide 49: Process Operations
What do operators need to do in order to control __________systems?
What are operation, monitoring, and maintenance priorities for a ______system?

## Slide 50: Corrosion Inhibitors
The use of phosphate corrosion inhibitors is common in drinking water
Purpose is to promote the formation of insoluble scales that prevent lead and copper from leaching from pipes
The most common corrosion inhibitors used are
Zinc orthophosphate
  Orthophosphate
  Polyphosphates
  Phosphate Blends
  Silicates

## Slide 51: Passivation is the Key for Most Utilities
Passivation is the formation of lead and copper carbonate films
  calcium carbonate film metal oxide film
  metallic carbonate film Phosphate/metallic/carbonate film
water
Film formation prevents galvanic cell reaction
Pipe wall

## Slide 52: Polyphosphate Has a Place in Managing Colored Water Complaints but Can Impact Lead Leaching
Median lead concentration (μg/l) after 30 min. contact with new Pb pipe at 25oC
Be careful not to overdose polyphosphate, or hydrocerussite
(hydrated lead carbonate) protective coatings will be damaged
o-PO4 dose | Zero poly-P | 0.2 mg/l poly-P | 1.6 mg/L poly-P
0 | 142 | 143 | 281
1 | 3 | 19 | 54
2 | 3 | 12 | 51
3 | 3 | 10 | 44
4 | 3 | 9 | 32
Effect of polyphosphate on orthophosphate dose response (Colin Hayes, Swansea Univ.)
Notes: Concentration without orthophosphate addition is high (compare to 15 ug/L action level). Orthophoshpate helps mitigate lead leaching. Higher doses of ortho + poly phosphate can mitigate both lead and colored water (data not shown on color/iron) but over-dosing polyphosphate actually worsens the lead problem. Thus, careful balance in operation is key.

## Slide 53: Edward’s Chloride-to-Sulfate Mass Ratio (CSMR) May be a Marker for Potential Lead Release
Chloride: Sulfate Mass Ratio
  < 0.58 = minor fluctuations less likely to impact leaching
  > 0.58 = minor fluctuations may impact lead leaching
  Especially important in RO permeate where very low CSMR may cause index to fluctuate above and below 0.58
Low Alkalinity also contributes to elevated risk
  High Alkalinity = no leaching
  Low Alkalinity = lead leaching
  Again, this may be key in RO permeate applications where blending can drastically reduce alkalinity in drinking water
Orthophosphate inhibitor can mitigate

## Slide 54: Flint Water was very corrosive. Detroit water was not.

## Slide 55: Corrosion Control Approach Begins with Proper Evaluation and Carries through Design and Operation
Holistic view
Evaluation
Understand the first principles (theory)
Desktop analysis – source to tap
Pipe loops, pipe rigs (use pipe from system)
Recommendations
Full-scale implementation
Monitoring
Feedback
Remember: There are no “corrosion indices,” surrogate pipe rigs, or water quality parameters, that can take the place of directly monitoring lead release.

## Slide 56: Corrosion Test Loops Can be Used to Evaluate Process Impacts
Pilot testing is recommended to evaluate alternative corrosion inhibitors
For DPR we need to look at blend ratios of water from supply sources
Typical corrosion pilot unit

## Slide 57: Coupon Studies Also Provide Insight

## Slide 58: Example Lead/Copper Corrosion Pilot Unit Built with Lead Solder
Copper piping with 50/50 lead solder for LCR samples

## Slide 59: Setup Allows Testing of Multiple Waters and/or Corrosion Control Treatment Strategies

## Slide 60: Key Factors in Lead and Copper Testing
Need a solid baseline of current drinking water chemistry
Need a solid baseline of likely DPR product water chemistry
The RTW Model (next slides) can be used to calculate corrosivity under various blend and operational scenarios
This can be used to determine water quality test conditions for pipe loops and corrosion control strategies

## Slide 61: The Tetra Tech RTW Model from AWWA
Input water quality data, including multiple chemical additions
Output provides a suite of corrosion indices
Program can calculate blended water quality conditions as well—useful for DPR
Originally Rothburg, Tamburini, and Windsor (RTW) Model

## Slide 62: “RTW Model” Can Be Used to Calculate Stability of Water
Ranges of water quality parameters are important but must be looked at holistically, not individually
Note that in some cases water quality parameters are in desired range but overall chemistry is still corrosive

## Slide 63: Operations Staff Should Have Acceptable Water Chemistry Boundaries but Cross-Check with RTW
Always follow prescribe dose rates for chemical
Always maintain acceptable pH, alkalinity, and other water quality targets
EPA Guidance Document (next slide) provides information on corrosion control
Stanford et al (2016) provides additional DPR-specific guidance
Any major changes should trigger need for lead/copper evaluation

## Slide 64: Detailed Corrosion Control Treatment Guidance is Available from EPA
Contains useful flow charts to help select viable treatment options
For an update, see also:
USEPA, March 2016 "Optimal Corrosion Control Treatment Evaluation Technical Recommendations for Primacy Agencies and Public Water Systems" Office of Water, EPA 816-B-16-003

## Slide 65: Three Corrosion Control Methods Originally Identified as Optimum in the Current LCR
Carbonate Passivation
Inhibitor Addition
Metal complexes on pipe surface
Prevents metal release
Phosphates (orthophosphate or blends)
Silicates
Carbonate Precipitation
Calcium carbonate coats pipe surface
Does not form uniform, non-porous layer
pH/alkalinity balance
Carbonate Precipitation Not Considered An Effective Strategy for LT-LCR Compliance
Notes: The original LCR guidance also identified 3 methods for corrosion control. These include:
Carbonate passivation (which is achieved through pH/alkalinity adjustment) induces the formation of less soluble metal compounds on the surface of the pipe, thereby preventing metal release.
Under inhibitor addition, utilities typically add orthophosphate or ortho/polyphosphate blends, which similar to carbonate passivation form low-solubility metal complexes on the surface of the pipe. Silicates can also be used, but there not as common as they are not typically as effective as PO4. I also want to note that polyphosphates are not generally recommended for controlling lead and copper corrosion as these have been found to accelerate lead and copper corrosion in most waters.
The final method is carbonate precipitation. Under this method, calcium carbonate precipitates form, coating and protecting the surface of the pipe.
What has been discovered more recently, however, is that carbonate scales may not deposit uniformly, and therefore, do not provide uniform protection against corrosion. In addition, there are difficulties in predicting the potential formation of calcium carbonate precipitates and in controlling the formation of scale buildup to ensure the hydraulic capacity is not significantly reduced. As such, carbonate precipitation is not considered an effective strategy for compliance with the long-term lead and copper rule.
Side note: There strategies that have been discussed (i.e., maintaining lead(IV) scales with high free chlorine residuals); however these are not recommended as primary CCT strategies for LT-LCR compliance due to the potential for stagnant water in the distribution system or home as well as other WW changes that may reduce free chlorine residuals. These are more likely to be considered as a companion technology to other CCT strategies or a tool in a larger toolbox, where the focus is holistic distribution system optimization.

## Slide 66: Lead and Copper Control Treatment Strategies
Systems adding phosphate
Boost phosphate
Adjust pH
Add phosphate and adjust pH
Add phosphate
Raise pH and/or alkalinity
Systems not adding phosphate
Switch to ortho-P
Adjust pH
Systems adding poly-phosphate
Notes: For this study, we classified systems into one of two categories: systems not adding phosphate and systems adding phosphate.
Lower pH – to try to achieve a pH with the range that is considered most effective for phosphates.

## Slide 67: Common, Functional Means of Changing Water Chemistry
Note: Other process chemicals can impact these parameters including coagulation, scale formation control for membranes, etc.
Increase pH
Caustic Soda (NaOH)
Slaked Lime (Ca(OH)2)
Decrease pH
Hydrochloric Acid (HCl)
Sulfuric Acid (H2SO4)
Add Alkalinity
Chemicals that increase pH also add alkalinity
Ortho-phosphate
Increase CCPP
Lime (CaO)
Carbon Dioxide (CO2)
Sodium bicarbonate (NaHCO3)
Depends on starting water chemistry
CO2 + NaOH
Methods can include:
CO2 + Slaked Lime
Calcium chloride + CO2 + NaOH
Note: Decreased pH decreases Alkalinity and CCPP
Safety: Always use proper personal protective equipment and follow chemical-specific protocols when handling acids and bases

## Slide 68: Unintended Consequences
Notes: Unintended consequences are unforeseen outcomes resulting from treatment changes that affect other aspects of the system. With increasing regulations on the distribution system and aging infrastructure, it is increasingly difficult to find the right balance of water quality and corrosion control to achieve simultaneous compliance.
Classic example in the lead and copper realm is well-intentioned switch from chlorine to chloramines.

## Slide 69: Potential Unintended Consequences of Control Strategies
Description of Potential Consequence | OCCT Strategy | 
 | pH/Alkalinity Adjustment | Phosphate Addition
Increased scaling resulting in loss of hydraulic capacity or additional system maintenance |  | 
Reduced distribution system disinfection performance |  | 
Increased microbial activity in the distribution system |  | 
Change in DBP speciation/concentrations and Joint Stage 2 DBPR and LT-LCR compliance |  | 
Increased phosphorus loading at WWTP, with increased sludge production |  | 
Altered metals loading to wastewater treatment plant |  | 
Need for additional operator certification/staffing |  | 
Notes: To the extent possible, water systems are expected to select CCT strategies that minimize the potential for consequences. In some instances, however, consequences may be unavoidable to
achieve compliance with the LT-LCR. Those unintended consequences are shown here and vary depending on the OCCT strategy implemented.
Scaling - Raising pH and/or increasing alkalinity has the potential to result in additional calcium carbonate precipitation. POST-PRECIPITATION OF SOLIDS BOUND WITH PHOSPHATE IN THE DISTRIBUTION SYSTEM – Aluminum, Iron, Manganese, etc
Disinfection performance: disinfection efficacy decreases at higher pH levels, suggesting that disinfection efficacy could be reduced if the pH were increased for corrosion control. So some systems may need to increase their secondary residual concentration/dose slightly
DBP: OCCT strategies involving an increased finished water pH have the potential to result in higher TTHM concentrations.
Stage 2: Striking the proper balance in pH to control both DBPs and corrosion could be one of the most challenging aspects of complying with the LT-LCR.
P: Addition or boosting of orthophosphate for corrosion control has the potential to increase the influent P concentration at POTWs. For those systems with biological treatment, increased P may require them to add chemical treatment to comply with permitted P limits.

## Slide 70: Process Monitoring Focuses on Managing Finished Water Stability
Online pH, temperature, TDS/conductivity let operations teams know about basic targets for stability
Laboratory staff support operations teams by providing additional periodic (daily) data on alkalinity, calcium, chloride, sulfate, etc. that allows detailed calculation of saturation index
Corrosion inhibitor feed (e.g., orthophosphate) is based on desired dose, plant flow rate, and pump set-point

## Slide 71: Recommendations
A corrosion control study should be performed under the following circumstances
If a new raw water source is activated
If blends change or are expected to change for DPR
If a new finished water supply is purchased (or if a utility will start selling finished water to a neighboring system)
If chemical treatment processes are changed in the plant. This could include the following:
    Changing pre-oxidants
    Increasing chlorine dose
    Switching distribution system disinfectant to chloramine
    Changing coagulants or increasing coagulant dose significantly

## Slide 72: Recommendations
A corrosion control study should be performed under the following circumstances:
Study should consider seasonal and diurnal effects
    Including raw water chloride levels
    Conduct well in advance of future treatment or operational changes that could impact lead or copper release

## Slide 73: Recommendations
The chloride to sulfate mass ratio should be examined if any treatment changes are implemented or blend changes. If this number increases above 0.58 then an orthophosphate inhibitor should be added.
The best inhibitor to use if lead is the controlling issue is likely ortho-phosphate (phosphoric acid). A zinc based product usually does not work any better and costs more and can cause issues for the wastewater treatment plant.
Polyphohphates can INCREASE lead levels as they work as a sequestering agents.

## Slide 74: Recommendations
Good operations
DO NOT cut inhibitor dosages to save money
DO NOT cut pH adjustment to save money
Keep feed equipment in good shape to minimize downtime
STABILITY is key
Prevent random variations in raw or finished water sources
Keep distribution system water quality stable
  Water age, tank turnover, flushing
  Operations teams want consistent pH, chlorine residual

## Slide 75: Equipment
What equipment is required?

## Slide 76: Equipment Descriptions
There are many different approaches to corrosion management and stability control
Specific equipment details are not included here, but the majority of processes are lime dosing, lime contactors, carbon dioxide addition and various liquid chemical doses.
Solids
Contact
Basin
CO2
Flocculation
Sedimentation
Lime
Recarbonation
Chlorine
Rapid Mix
Filters
To System
Surface
Water
Single-Stage Lime Treatment Process

## Slide 77: Critical Control Point Response Procedures
Critical Control Point Response Procedures
What are the critical monitoring and response procedures?

## Slide 78: Critical Control Point Response Procedures
These response procedures are generic, and taken from WRF project Reuse-13-03. For a specific project, they can be amended to suit the plant specifics. They are shown here as examples of particular approaches to treated water stabilization, in this case based on lime/CO2 dosing downstream of RO.

## Slide 79: Alert Response

## Slide 80: Critical Response

## Slide 81: Safety
What safety considerations are specific to corrosion control?

## Slide 82: Safety Considerations Are Focused on Chemical Exposure
The main risk to operators is chemical exposure due to spills, splashes, or plumbing failures
Closed toed shoes, protective clothing, gloves and eye protection are required at a minimum when handling chemicals
  Some chemicals may require additional full face mask/splash guard, elbow-length gloves, and additional protective outerwear such as Tyvek
Consult material safety data sheets for detailed handling information and spill response

## Slide 83
The Water Research Foundation (WRF) is a nonprofit (501c3) organization which provides a unified source for One Water research and a strong presence in relationships with partner organizations, government and regulatory agencies, and Congress. The foundation conducts research in all areas of drinking water, wastewater, stormwater, and water reuse. The Water Research Foundation’s research portfolio is valued at over $700 million.
The Foundation plays an important role in the translation and dissemination of applied research, technology demonstration, and education, through creation of research-based educational tools and technology exchange opportunities. WRF serves as a leader and model for collaboration across the water industry and its materials are used to inform policymakers and the public on the science, economic value, and environmental benefits of using and recovering resources found in water, as well as the feasibility of implementing new technologies.
For more information, contact:
The Water Research Foundation
Alexandria, VA Office
1199 North Fairfax Street, Suite 900
Alexandria, VA 22314-1445
Tel: 571.384.2100
www.werf.org werf@werf.org
Denver, CO Office
6666 West Quincy Avenue
Denver, Colorado 80235-3098
Tel: 303.347.6100
www.waterrf.org Info@WaterRF.org
© Copyright 2018 by The Water Research Foundation. All rights reserved. Permission to copy must be obtained from The Water Research Foundation.
WRF ISBN: 978-1-60573-363-0
WRF Project Number: Reuse-15-05/4772
This report was prepared by the organization(s) named below as an account of work sponsored by The Water Research Foundation. Neither The Water Research Foundation, members of The Water Research Foundation, the organization(s) named below, nor any person acting on their behalf: (a) makes any warranty, express or implied, with respect to the use of any information, apparatus, method, or process disclosed in this report or that such use may not infringe on privately owned rights; or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of, any information, apparatus, method, or process disclosed in this report.
Hazen and Sawyer, Carollo Engineers Inc., Santa Clara Valley Water District
This document was reviewed by a panel of independent experts selected by The Water Research Foundation. Mention of trade names or commercial products or services does not constitute endorsement or recommendations for use. Similarly, omission of products or trade names indicates nothing concerning The Water Research Foundation's positions regarding product effectiveness or applicability.