## Slide 1
Membrane Filtration (Microfiltration and Ultrafiltration)

## Slide 2: Project Partners
Hazen and Sawyer
Carollo Engineers
Santa Clara Valley Water District
LA Sanitation District
Gwinnett County (GA)
El Paso Water Utilities
UFTREEO (University of Florida)
Sacramento State
University of Arizona-WEST Center
TrojanUV
Xylem Inc.
Process Applications Inc.
Calgon Carbon Corporation

## Slide 3: Note To Trainers and Students
Membrane filtration content is well-covered by existing training programs such as the membrane operator courses developed by private companies and membrane organizations
As such, the content provided within this module is meant to provide supplemental material that is specific to direct potable reuse that should be adapted for inclusion in other training courses
This is NOT a stand-alone module
No information contained in this module should be taken as a complete training course on membrane filtration

## Slide 4: Introduction and Fundamentals

## Slide 5: Low Pressure Membrane Systems is Part of Training Material Offered by…
SWMOA – South West Membrane Operator’s Association SEDA – South East Desalination Association SCMA – South Central Membrane Association NWMOA – North West Membrane Operator’s Association (Details attached at end of presentation) Other membrane organizations – Such as the North West Membrane Association, International Desalination Association

## Slide 6: Membrane Filtration Role in Potable Reuse

## Slide 7: Membranes Have Been Used for Advanced Treatment including Potable Reuse for More than 40 Years
Membranes deliver consistently high quality water
1976: Orange County Water District: Water Factory 21, Fountain Valley, CA
Photo Source: OCWD Water Factory 21 Brochure, Circa 1984

## Slide 8: Membrane Filtration and RO-Based Reuse Processes
Membrane filters provide critical fouling protection for the RO including particulate removal and enhanced control of biofouling.
As RO material moved from cellulose acetate to thin film composite (TFC) polyamide, there was a greater emphasis of pretreatment as free chlorine to control biofouling could no longer be used (incompatible with TFC) and a smaller membrane spacer was more susceptible to particulate fouling.
Successful US demonstration testing at Reedy Creek, Florida and Orange County, California led to full scale implementation of MF as pretreatment to RO at early potable reuse facilities in the late 1990s.
Membrane Filters Enabled Thin Film Composite (TFC) RO Membrane Use in Potable Reuse Applications
1998: Siemens 90M10C
Scottsdale Water Campus AWT, Scottsdale, AZ

## Slide 9: Non-RO Reuse Examples with Membrane Filtration
Surface Water Augmentation: 60 MGD
  Lake augmentation at Lake Lanier (Atlanta’s Water Supply)
  Tight phosphorus limits to prevent eutrophication (0.08 mg/L)
  Membrane filtration removes unsettled ferric hydroxide and bound phosphorous.
Treatment:
  Secondary WWTP plus Coag-Filtration, MF, Ozone, GAC(BAC), Ozone
Gwinnett County, F. Wayne Hill WRC, Buford, GA
2006: F. Wayne Hill WRC, Buford, GA

## Slide 10: RO Membrane-Based Treatment Train (MF-RO-UV/AOP) Provides Multiple Barriers for Pathogens and Chemicals
Removes Pathogens
Removes Salinity, Pathogens, Chemicals
Disinfects (Pathogens), Oxidizes Chemicals
Final Disinfection
NaOCl?

## Slide 11: RO-Based Reuse Example
2013: 2 MGD Direct Potable Reuse
CRMWD, Raw Water Production Facility, Big Spring , TX

## Slide 12: Log Removal Credit (LRV, US Basis) Summed Across Multiple Barriers (Maximum Creditable)
 | ClNH2 | MF | RO | UV/AOP | Cl2 | Total
Virus | 0 | 0 | 1-2 | 6 | 4 | 11-12
Crypto | 0 | 4 | 1-2 | 6 | 0 | 11-12
Giardia | 0 | 4 | 1-2 | 6 | 3 | 14-15
Table and Graphic via Project Reuse-13-03

## Slide 13: Other Process Components Serve an Operational Objective of Maintaining Assets and Plant Production Capacity
Limits Biological Fouling
Removes Large Particles
Protects RO Membranes from Particulate Fouling
Protects RO Membranes from Scale Formation
Protects pipes and distribution system from corrosion
NaOCl?

## Slide 14: Membrane Filtration Operating and Design Concepts

## Slide 15: The Filtration Spectrum
Microfiltration
10 um – 100 nm
Ultrafiltration
100 - 10 nm
Nanofiltration
10 - 1 nm
Reverse Osmosis
< 1 nm
colloids viruses
color
hardness pesticides salts
water
giarda
crypto
bacteria
colour
hardness
pesticides
salts
water
colloids
viruses
salts
water
color
hardness
pesticides
salts
water
Source: Pentair - Norit Membranes

## Slide 16: Membrane Filtration
Membrane material forms a physical barrier that strains particles from a treatment stream
  Typically membrane filtration refers to Microfiltration (MF) and Ultrafiltration (UF) ranges
  Particles larger than membrane pores are retained
  Smaller particles pass through the membrane
  Retained particles are recovered during cleaning

## Slide 17: Straining Example
Objects small enough to fit through membrane pores will pass thru membranes

## Slide 18: Two Primary Membrane Filtration Modes of Operation
Membrane Filtration Uses Crossflow or Dead End Filtration

## Slide 19: Some Membranes are Designed for Crossflow and Dead End Operation
Crossflow can be beneficial for systems that experience high solids loading
  For reuse applications, high solids loading can occur during clarifier upsets
Some membrane element designs allow systems to operate with and without crossflow.
Source: Pall Corporation/Asahi

## Slide 20: Many Commercial Membrane Materials Are…
Polymeric
  Polyethersulfone (PES)
  Polyvinylidene Fluoride (PVDF)
  Teflon (PTFE)
  Polyvinyl Chloride (PVC)
  Polypropylene (PP)
Ceramic
  Silicon Carbide (SiC)
  α-Aluminum Oxide
  Zirconium
  Titanium Dioxide
Source: Pentair
Source: BASF/inge
Source: Liqtech

## Slide 21: Commercial Membrane Types and Configurations
Membranes
  Hollow Fiber
  Spiral Wound
  Tubular
  Flat Sheet
Unit Configurations
  Pressurized
  Submerged
  Canister
  Horizontal
  Vertical
Source: Kubota
Source: Pentair
Source: Memcor
Source: Polymem

## Slide 22: Dominant Potable Reuse Design: Hollow Fiber Membrane Filtration
Similarities and differences among product design
Fiber Bundle
Potting
Membrane Fiber

## Slide 23: Two Dominant Train Types
Pressurized vs. Submerged
Big Spring RWPF, Pressurized Pall/Asahi Trains
Source: GE/Zenon, 500D Submerged Train Design
Evoqua Submerged Train at OCWD

## Slide 24: Membrane Concepts and Terminology

## Slide 25: Membrane Water Flux
The amount of water passed through a unit of area over time
  Gallons per square foot per day (gfd)
  Liters per square meter per hour (LMH)
Flux is the same as surface loading rate for a conventional filter (gpm/ft2)
Sustainable flux rate is a function of water quality and cleaning system performance
Conventional: 4 gpm/ft2 = 5760 gfd
MF/UF: 60 gfd = 0.04 gpm/ft2
Source: Pentair
Courtesy Separation Processes Inc

## Slide 26: Transmembrane Pressure (TMP)
Pressure drop across a membrane
  Pressurized System: 3 - 45 psig, supplier dependent
  Submerged Systems: -2 to -12 psid, limited by elevation and suction losses
Source: Boysen

## Slide 27: TMP doesn’t tell the whole story…
Flux (velocity) has a strong impact on head loss
Temperature (viscosity) has a strong impact on head loss
Neither are constant. We need to work with the data to compare data points…

## Slide 28: Permeability
Sometimes called Specific Flux
Permeability measures the amount of pressure required to produce flux
Different for different membrane products
Permeability accounts for changes in flow
Corrected for temperature
Resistance sometimes used – inverse of permeability
Filter cake picture adapted from Veolia

## Slide 29: Temperature Correction Factor (TCF)
Viscosity is critical
  TCF uses a ratio of actual viscosity to a reference viscosity.
Typical reference temperature for MF/UF is 20oC
  At 20oC (68oF), the viscosity of water is approximately 1 cP… at 4oC (40oF), 1.6 cP

## Slide 30: Temperature Correction Factor
Chart: Temperature Correction Factor
| 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65
 | 1.7194 | 1.5098 | 1.3257 | 1.1641 | 1.0222 | 0.89761 | 0.78818 | 0.6921 | 0.60773 | 0.53364 | 0.46859 | 0.41147 | 0.36131 | 0.31726
Temperature, oC
TCF

## Slide 31: Normalized TMP and Permeability
Temperature and flow related differences are eliminated
Chart: Temperature Correction Factor
| 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65
 | 1.7194 | 1.5098 | 1.3257 | 1.1641 | 1.0222 | 0.89761 | 0.78818 | 0.6921 | 0.60773 | 0.53364 | 0.46859 | 0.41147 | 0.36131 | 0.31726
Note to also take into account any height difference between measurement points.

## Slide 32: Monitoring Membrane Filter Plant Operation
Key Variables
  Normalized Permeability: are the membranes operating as they should ?
  TMP: are we approaching damaging conditions?
  Integrity Testing Result: have the membranes been damaged?

## Slide 33: Filtration Mechanism Review
Three Main Types
  Pore Plugging
  Alternative Path (Depth)
  Cake Formation
Source: Boysen, SEDA 2009 Spring Symposium
Courtesy Separation Processes Inc

## Slide 34: Review: Alternative Path (Depth) Filtration
Concept:
  Depth filtration occurs when particles become entrapped in the matrix of the filter media
  Fluid flow seeks the path of least resistance, as less restrictive paths are blocked by filtered particles, flow area shrinks and hydraulic resistance increases
  Depth filtration occurs when filter media has a broad distribution of pore sizes
  Efficiency increases with pressure drop
Source: Boysen, SEDA 2009 Spring Symposium
Courtesy Separation Processes Inc

## Slide 35: Review: Pore Plugging
Concept:
  Filter acts as a screen with minimal depth and uniform openings
  Plugging occurs as the filter intercepts the particles and reduce the available filtration area
  Pore plugging occurs when filtered particles are approximately the same size as the filter pores
  Efficiency stays the same with increasing pressure drop
Source: Boysen, SEDA 2009 Spring Symposium
Courtesy Separation Processes Inc

## Slide 36: Review: Cake Formation
Concept:
  Cake formation occurs when particles larger than the pores in the media are collected on the surface of the media
  Differential pressure increases as cake thickness increases
  If filtered particles have high flow resistance, cake formation is not favored
  Efficiency controlled by cake layer
Source: Boysen, SEDA 2009 Spring Symposium

## Slide 37: Filtration Mechanisms
Primary mechanism almost always cake formation
Pore plugging is highly unfavorable
Depth filtration unlikely
Monitoring TMP can help identify foulant/mechanism

## Slide 38: Potable Reuse Membrane Filtration Operations

## Slide 39: Typical Membrane Cycle of Operations
Filtration
Backwash
Maintenance
Clean
Clean in
Place
Source: Boysen, SCMA Annual Meeting 2016

## Slide 40: Typical Performance Data Reinforcement
TMP and Permeability
TMP trends typically increase as foulant accumulates during filtration, follow a sawtooth pattern as backwashing removes the foulant.
Permeability trends follow a sawtooth pattern inverse to the TMP trend creating an s-curve over time.

## Slide 41: Types of Foulants
Main UF Foulant Types
  Particulate/Colloidal
  Organic
  Biological
  Scale
Size and Type generally dependent on source and pretreatment methods
Differences between secondary and tertiary effluent?
Iron Fouling - Gwinnett County, F. Wayne Hill WRC, Buford, GA (2015)

## Slide 42: Purpose of Autostrainers
We often think of grit, but neutrally buoyant particles can also be problematic in reuse applications
Water Campus Strainer Refurbishment, Scottsdale, AZ (2012)

## Slide 43: High Solids Loading
Pathways to broken fibers
  Large sharp objects abrade membranes
  Solids accumulate near pots – even fine particles can cause abrasions during backwashing due to membrane rubbing on solid materials
  If TMP exceeds critical TMP, membrane element damage will occur
Membrane Integrity Inspection Peoria, AZ (2011)

## Slide 44: More on Critical TMP
Critical TMP can lead to membrane element failure.
Even if critical TMP is not exceeded, running at highly cyclic TMP can result in cyclic fatigue of components
Source: Eric Owens, SPI/West Basin
Cracked pot from excessive TMP, Scottsdale, AZ (2012)

## Slide 45: Protecting Membrane Life
Loss of integrity
  Water quality is impacted
Loss of permeability
  Production is impacted
    More frequent CIP
    More downtime
    High cost operations
How membranes typically fail
Membranes with Irreparable Integrity, Scottsdale, AZ (2010)

## Slide 46: What Causes Fiber Breaks?
Mechanical Damage
  Feed Strainer Failure
  Filtrate Debris
Operational Processes
  Backwashing
  Cyclic Aeration
  Hydraulic Anomalies (Air & Water Hammer)
  Temperature
Cleaning Processes
  Oxidation
Membrane Composition
  Symmetry
  Material
  Manufacturing
  Potting
Source: Toray
Sand Packed Potting in ZW500D, Scottsdale, AZ (2009)
Courtesy Separation Processes Inc.

## Slide 47: Types of Fiber Breaks
Cut Fiber
Separation at Potting
Delamination
Puncture
Sidewall Blowout
Packing with Solids
Courtesy Separation Processes Inc

## Slide 48: Detecting Fiber Breaks
Pressure Decay Test
Vacuum Decay Test
Diffusive Flow Test
Water Displacement Test
Manufacturer Developed Empirical Test
Manufacturer Developed Demonstration Test
Spiked Inert Particle Test
Molecular Marker Test
Direct Integrity Test Methods
Courtesy Separation Processes Inc.

## Slide 49: Pressure Decay Testing
Integral
Breached
Courtesy Separation Processes Inc.

## Slide 50: Pressure Decay Testing
Advantages Include
  Test all modules within unit
  Sensitivity on the order of single fiber breaks
  Standard for most MF and UF systems
  Automated
  Widespread acceptance
  Ability to test both the membrane and piping for leaks
Units
  psi/min
Courtesy Separation Processes Inc.

## Slide 51: Understanding Integrity Testing and Log Removal
Based on bubble point principle
Liquid Held in Pores by Surface Tension and Capillary Forces
Minimum Air Pressure required to force liquid out of the pores is a measure of the pore diameter
P = [4kcos(q)s]/d
P = bubble point pressure
d = pore diameter
k = shape correction factor
Cos θ = liquid contact angle
σ = surface tensionσ
Bubble Point of MF/UF membrane with
0.2 um pore is 40 psi
0.02um pore is ~1900 psi
Bubble Point of 4 um hole is ~ 6 psi

## Slide 52: Understanding Integrity Testing and Log Removal
Pressures to verify actual pore sizes can be impractical.
The industry wide standard tests all MF/UF system to the same benchmark – 3 microns (approx. size of cryptosporidium). This is an industry equalizer.
(ASTM D6908) “Standard Practice for Integrity Testing of Water Filtration Membrane Systems”.
USEPA – Membrane Filtration Guidance Manual – Nov 2005.

## Slide 53: Understanding Integrity Testing and Log Removal
How to Calculate Log Removal?
Need to estimate the breach
Appendix X1 ASTM 6908-6
(Temperature)

## Slide 54: Reuse Application Permeability Loss
Biological fouling can significantly impact membrane performance.
  Excreted polymers (EPS) can be sticky and difficult to remove from the membranes
Chloramines are primary control
  Chloramine demand can change during upsets
  Influent ammonia changes seasonally and with upsets
Continuous disinfectant strategies can strengthen the microbial community and cause immunity
Biological fouling can be problematic
Evidence of biological fouling: pink membranes
Scottsdale, AZ (2012)

## Slide 55: Critical TMP
Usually causes irreversible damage
Cracked potting and replacement membranes during high fouling event, Scottsdale, AZ (2012)

## Slide 56: Potable Reuse Membrane Filtration Operations and Monitoring

## Slide 57: What are the keys?
Normal Operation
  Establish upset indicators
  Evaluate normalized trends over a long enough scale to compare performance
  Monitor direct integrity testing. Identify long term issues
Cleaning
  Reduce Variables: Perform all CIPs the same to compare cleaning effectiveness
  Perform Multiple Cleans when needed
  Use Clean Water Flux Testing to evaluate long term effectiveness

## Slide 58: Clean Water Flux Testing
Can be used to establish baseline membrane performance
  This can be used to enforce membrane warranty
Evaluate Cleaning Effectiveness
Chart Membrane Life
  Plan / budget for membrane replacement
Performed by operating the rack at 25%, 50%, 75%, 100%, and 125% of the design flux.
Ideally - performed before and after each clean
Ideally - will have a “clean” water source, i.e. potable
  This will provided a relatively repeatable water quality
  If potable is not available, can us feed water
Courtesy Separation Processes Inc.

## Slide 59: Clean Water Flux Testing
The slope of the lines in this chart is flux/TMP, or permeability
CWFT when new
Subsequent tests over time

## Slide 60: Permeability Monitoring
A long range is required to evaluate process stability

## Slide 61: MF Data Collection
Shorter ranges help assess daily operations and processes… Is there anything unusual in this data?

## Slide 62: Inspect Each Process
Are Chemically Enhanced Backwashes Performing Effectively?

## Slide 63: Integrity Test Results
A small amount of scatter is normal

## Slide 64: Other Considerations: Cleaning and Membrane Repair

## Slide 65: Chemical Clean in Place
High pH cleaning using sodium hypochlorite and sometimes caustic to increase cleaning pH is typically utilized – removes organic, biological and solid material.
Low pH cleaning with citric acid and sometimes an inorganic acid to lower pH is typically utilized. Useful to remove iron fouling and any scale formation.
RO permeate is often available, if not a softening system may be required to manage scaling from hardness if filtrate is utilized for cleaning above pH 10.5.
Neutralized CIP solution is often recycled to the head of the reclamation process.
Some general considerations. Other training programs provided greater breadth and depth
Membrane Building Chemical Storage, F. Wayne Hill WRC, GA (2016)

## Slide 66: Membrane Repair
In potable reuse applications, membrane isolation and fiber repairs are more critical
  Membrane isolation is possible in most train designs, allowing membranes with integrity failure to be removed/repaired while the system is operational
  Access and Safety are primary considerations while removing and repairing the membranes
  Coordination and planning of these repairs should be performed before repairs are attempted
Membrane Pinning, Pinellas County WTE IWTP, St. Petersburg, FL (2016)

## Slide 67: Critical Control Response Procedures

## Slide 68: Hazard Analysis and Critical Control Point (HACCP) History
Systematic preventative approach to Food Safety
Focus on barriers – not end of pipe treatment
Adapted to IPR and DPR through projects WRRF-09-03 and Reuse-13-03
Conceived in 1960s by Pillsbury for NASA
Defined in ISO 22000 – Food Safety

## Slide 69: A CCP Approach Focus on Health Relevant Contaminants

## Slide 70
CCPs are points in the treatment process that are specifically designed to reduce, prevent, or eliminate a human health hazard and for which controls exist to ensure the proper performance of that process
The CCP process is the barrier.

## Slide 71: Example Critical Control Point - MF
Chart: MF Filtrate Turbidity
| 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24
MF Filtrate Turbidity | 0.004 | 0.003 | 0.003 | 0.005 | 0.006 | 0.0065 | 0.015 | 0.02 | 0.021 | 0.021 | 0.021 | 0.021 | 0.021
Alert | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007
Critical | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Risk : Microorganisms (cryptosporidium and giardia)
MF will use pressure decay integrity test (sensitive) and filtrate turbidity as back up (less sensitive)

## Slide 72: Membrane Filtration – Critical Control Points Example
Pathogen removal is critical in potable reuse
Membrane integrity is the barrier
  Protozoa LRV of 5-6 is achievable with fully intact membrane barrier
Direct Integrity Testing (DIT) is a primary monitor
  DIT can detect 1-5 broken fibers per membrane filtration unit
Turbidity is often a secondary monitor of integrity
  Much lower resolution, identification of significant integrity failures
Protection of Health through Biological Constituent Removal
Source: Reuse-13-03 HACCP Testing, Scottsdale, AZ (2015)

## Slide 73: MF Alert (Warning) Response

## Slide 74: MF Critical Alarm (Failure) Response

## Slide 75: Design Criteria

## Slide 76: Design criteria for membrane filtration units and elements is included in the existing training material available as noted previously
Additional considerations that should be considered for potable water reuse systems include
  Integrity Monitoring. More critical for potable reuse than other applications. Provide AHT capabilities and consider individual unit turbidity analyzers as secondary monitor for integrity.
  Membrane Repair. Provide adequate access for membrane repair or pinning station.
  Flux Basis. Typical designs have used a maximum instantaneous flux basis between 20 and 45 GFD depending on membrane supplier and process, demonstration testing at flux basis of up to 65 GFD have been successful.
  NSF Requirements. Regardless of regulatory requirements, use of NSF components is a consideration since ultimate water destination is potable reuse. This would be a typical requirement for potable water systems. Most notable issues have been with rubber expansion couplings.
  Compatible Materials: O-ring gasket material must be compatible with chloramines used for biological fouling control.
Source: Proco Products, Inc.

## Slide 77: Operation and Maintenance

## Slide 78: Operation and Maintenance items are included in the existing training material previously mentioned
Additional considerations that should be considered for potable water reuse systems include…
  Membrane Repairs: More critical for potable reuse than other applications
    Texas requires multiple passing air hold test results per day. There are implications of off spec water and engineered buffer requirements/off spec water disposal related to time in service. Operations must be prepared to perform membrane pinning more frequently or be capable of operating without the unit until fiber repairs can be made.
  Alarm Flooding: Number of alarms increases with process complexity
    Membrane filtration systems are highly automated. The number of alarms needs to be managed through proper design checks like HACCP.

## Slide 79: Safety

## Slide 80: Membrane Filter System Safety Concerns
The following safety concerns have been identified for membrane filtration system operation
  Noise Exposure
  Chemical Exposure
  Fall Hazards
  Overhead, Caught Between and Struck By Hazards
  Electrical Hazards

## Slide 81: Introduction to Membrane Filtration (South Central Membrane Association – Low Pressure Membrane Systems Handbook for Membrane Plant Operator Training, Module 3 Course details.

## Slide 82: Low Pressure Membrane Systems Handbook for Membrane Plant Operator Training
Chapter 1 – Introduction to Microfiltration and Ultrafiltration
1.0 Introduction
1.1 History of MF/UF
1.2 MF/UF Classifications
1.3 Membrane Manufacturers
1.4 Applications of MF/UF Systems
Chapter 2 – Terms and Definitions
Chapter 3 – Pretreatment

## Slide 83: Low Pressure Membrane Systems Handbook for Membrane Plant Operator Training
Chapter 4 – Operating Membrane Systems
4.0 Introduction
4.1 Loading, Start-up and Operation
4.2 Integrity Testing
4.3 Normal Operation Shutdown
4.4 Operational Challenges

## Slide 84: Low Pressure Membrane Systems Handbook for Membrane Plant Operator Training
Chapter 5 – Data Collection and Normalization
5.0 Data Collection and Normalization
5.1 Start-up Data / Baseline Data
5.2 Record Keeping Plan
5.3 Normalization of MF/UF Performance Data
5.4 Example of Normalized Data

## Slide 85: Low Pressure Membrane Systems Handbook for Membrane Plant Operator Training
Chapter 6 – Membrane Troubleshooting
6.0 Introduction
6.1 Alarm Systems
6.2 Alarm Corrections
6.3 Troubleshooting Alarms
Chapter 7 – Maintenance & Replacement of MF/UF Membranes
7.0 Introduction
7.1 Module Maintenance
7.2 Module Replacement

## Slide 86: Low Pressure Membrane Systems Handbook for Membrane Plant Operator Training
Chapter 8 – Membrane Cleaning
8.0 Introduction
8.1 Membrane Fouling and Scaling
8.2 Organic Fouling
8.3 Scaling and Organic Fouling
8.4 Raw Water Supply and Pretreatment Effects
8.5 Chemical Conditioning
8.6 Bacteria and Organic Debris
8.7 When to Clean
8.8 Clean in Place (CIP)

## Slide 87
The Water Research Foundation (WRF) is a nonprofit (501c3) organization which provides a unified source for One Water research and a strong presence in relationships with partner organizations, government and regulatory agencies, and Congress. The foundation conducts research in all areas of drinking water, wastewater, stormwater, and water reuse. The Water Research Foundation’s research portfolio is valued at over $700 million.
The Foundation plays an important role in the translation and dissemination of applied research, technology demonstration, and education, through creation of research-based educational tools and technology exchange opportunities. WRF serves as a leader and model for collaboration across the water industry and its materials are used to inform policymakers and the public on the science, economic value, and environmental benefits of using and recovering resources found in water, as well as the feasibility of implementing new technologies.
For more information, contact:
The Water Research Foundation
Alexandria, VA Office
1199 North Fairfax Street, Suite 900
Alexandria, VA 22314-1445
Tel: 571.384.2100
www.werf.org werf@werf.org
Denver, CO Office
6666 West Quincy Avenue
Denver, Colorado 80235-3098
Tel: 303.347.6100
www.waterrf.org Info@WaterRF.org
© Copyright 2018 by The Water Research Foundation. All rights reserved. Permission to copy must be obtained from The Water Research Foundation.
WRF ISBN: 978-1-60573-363-0
WRF Project Number: Reuse-15-05/4772
This report was prepared by the organization(s) named below as an account of work sponsored by The Water Research Foundation. Neither The Water Research Foundation, members of The Water Research Foundation, the organization(s) named below, nor any person acting on their behalf: (a) makes any warranty, express or implied, with respect to the use of any information, apparatus, method, or process disclosed in this report or that such use may not infringe on privately owned rights; or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of, any information, apparatus, method, or process disclosed in this report.
Hazen and Sawyer, Carollo Engineers Inc., Santa Clara Valley Water District
This document was reviewed by a panel of independent experts selected by The Water Research Foundation. Mention of trade names or commercial products or services does not constitute endorsement or recommendations for use. Similarly, omission of products or trade names indicates nothing concerning The Water Research Foundation's positions regarding product effectiveness or applicability.