## Slide 1
Reverse Osmosis (RO) Membranes

## Slide 2: Project Partners
Hazen and Sawyer
Carollo Engineers
Santa Clara Valley Water District
LA Sanitation District
Gwinnett County (GA)
El Paso Water Utilities
UFTREEO (University of Florida
Sacramento State
University of Arizona-WEST Center
TrojanUV
Xylem Inc.
Process Applications Inc.
Calgon Carbon Corporation

## Slide 3: Note To Trainers and Students
RO membrane content is well-covered by existing training programs such as the membrane operator courses developed by private companies and membrane organizations
As such, the content provided within this module is meant to provide supplemental material that is specific to direct potable reuse that should be adapted for inclusion in other training courses
This is NOT a stand-alone module
No information contained in this module should be taken as a complete training course on RO membranes

## Slide 4: Role in Potable Reuse

## Slide 5: What Does the CCP Approach Provide?
Focus is on health relevant contaminants

## Slide 6: RO Membrane-Based Treatment Train (MF-RO-UV/AOP) Provides Multiple Barriers for Pathogens and Chemicals
Removes Pathogens
Removes Salinity, Pathogens, Chemicals
Disinfects (Pathogens), Oxidizes Chemicals
Final Disinfection

## Slide 7: Log Removal Credit (LRV, US Basis) Summed Across Multiple Barriers (Maximum Creditable)
 | ClNH2 | MF | RO | UV/AOP | Cl2 | Total
Virus | 0 | 0 | 1-2 | 6 | 4 | 12
Crypto | 0 | 4 | 1-2 | 6 | 0 | 12
Giardia | 0 | 4 | 1-2 | 6 | 3 | 15

## Slide 8: Other Process Components Serve an Operational Objective of Maintaining Assets and Plant Production Capacity
Limits Biological Fouling
Removes Large Particles
Protects RO Membranes from Particulate Fouling
Protects RO Membranes from Scale Formation
Protects pipes and distribution system from corrosion

## Slide 9: RO and NF Operating and Design Concepts

## Slide 10: The Filtration Spectrum
Microfiltration
10 um – 100 nm
Ultrafiltration
100 - 10 nm
Nanofiltration
10 - 1 nm
Reverse Osmosis
< 1 nm
colloids viruses
color
hardness pesticides salts
water
giarda
crypto
bacteria
color
hardness
pesticides
salts
water
colloids
viruses
salts
water
color
hardness
pesticides
salts
water
Source: Pentair - Norit Membranes

## Slide 11: Desalination Technology

## Slide 12: Two Types of Desalination Process – Thermal or Membrane
Multi Stage Flash Distillation (MSF)
Multi Effect Distillation (MED)
Mechanical Vapor Compression (MVC)
Reverse Osmosis (RO)
Electro Dialysis Reversal (EDR)

## Slide 13: Desalination – Membrane Processes – Reverse Osmosis

## Slide 14: RO Membranes Provide Rejection of Small Molecular Weight Compounds
0.001
0.1
1.0
10
0.01
Size Ranges of Membrane Processes and Contaminants
Bacteria
Sand
Viruses
Salts
Nanofiltration
Reverse Osmosis
Membrane Processes
Typical Size Range of Selected Water Constituents
Micron Scale
Ultrafiltration
Microfiltration
100
Colloids
Cryptosporidium
Giardia
Dissolved Organics
Molecular Weight
200
100
20,000
100,000
500,000

## Slide 15: What is Osmosis?
Salty Water
Fresh Water
Membrane
(Prevents passage of salt)
Concentrated
Fresh Water
Diluted
Salty Water

## Slide 16: What is Reverse Osmosis?
Fresh Water
Concentrated
Salty Water
Applied
Pressure
Applied
Pressure

## Slide 17
Species Concentration Osmotic Pressure () (mg/L) (psi)
NaCl 1,000 14.5
LiCl 1,000 23.2
MgSO4 1,000 3.6
Sucrose 1,000 0.2
Seawater 35,000 390.0
Osmotic Pressures of Some Solutions
Van’t Hoff Equation

## Slide 18: Membranes Types and Operating Pressure
0
200
400
600
800
1000
1200
SWRO
BWRO
LP-RO
NF
Feed Pressure (psi)
Increased feed salinity
Increased salt rejection

## Slide 19: Different Types of RO Membrane – Based on Ability to Remove Salt
Quality Considerations (Eg DOW family of membranes)
  NF 270
  NF 90
  BW 30 (Low Energy)
  BW 30
  SW 30 (Low Energy)
  SW 30HR (High Rejection)
NF = Nanofiltration
BW = Brackish Water RO
SW = Seawater RO
Decreasing salt passage
(i.e. lower salinity product)
Generally increased pressure
Target divalent ions, macromolecules while allowing salt passage.
Many specifically tailored.

## Slide 20: Spiral Wound RO and NF Elements

## Slide 21: RO Membrane is Manufactured as a Flat Sheet

## Slide 22: Membrane Structure – Semi Permeable
Membrane Cross-Section
100,000 X Magnification
FABRIC
0.1 micron Polyamide
75 micron Polysulfone
2000 micron Polyester Fabric

## Slide 23
RO/ NF Membrane Separation Mechanism
Feed Flow
Na+
H2O
H2O
H2O
Cl-
H2O
H2O
Cl-
H2O
H2O
H2O
Na+
H2O
Na+
Concentrated
Salts
Permeate
SO42-
Cl-
H2O
Ca2+
HCO3-
RO Membrane Separation Mechanism
Courtesy Separation Processes Inc

## Slide 24: RO Membrane – Configured as Spiral Wound Element
Most common way to package membrane.
Maximizes surface area of membrane into plant footprint
Convenient to manage flow streams.

## Slide 25: Making a Spiral Wound Membrane
Step 1
Salty
Water
Membrane
Fold
Step 2
Fresh
Water
Fresh
Water
Salty
Water
Salty
Water
Permeate Spacer

## Slide 26: Making a Spiral Wound Membrane
Step 3
Permeate tube
with holes
Step 4
Fresh
Water
Salty
Water
Salty
Water
Salty
Water
Fresh
Water
Salty
Water
Salty
Water

## Slide 27: Making a Spiral Wound Membrane
Step 5
Step 6
Salty
Water
Fresh
Water
Fibreglass
casing
Salty
Water
Salty
Water
Fresh
Water
Brine Spacer

## Slide 28
Feed flow perpendicular to spiral
Permeate collected to permeate tube.
Permeate flows down permeate channel
Feed permeates through membrane surface

## Slide 29
Finished RO Membranes
Diameter (inches) | Typical Applications
2.5 | Small domestic applications < 1 gpm
4 | Small plants, pilot units. < 10 gpm
8 | Most common size for large applications > 10 gpm
16 & 18 | Very large plants. Recent development. > 25 mgd
Koch Membrane Systems
Hydranautics
Notes: 29

## Slide 30
Reverse Osmosis Element Pressure Vessel Assembly
Feed
Concentrate
Permeate
Head
End Adapter
R.O. Element
Interconnector
O-rings
Brine Seal
Pressure Vessel
Retaining Ring
Head Seal
Thrust Cone
Courtesy Separation Processes Inc.
Notes: 30

## Slide 31: Pressure Vessels Assembled to ASTM Requirements and Rated by Feed Pressure

## Slide 32: RO Skid Consist of Multiple Pressure Vessels Arranged in Stages
Town of Jupiter – Nanofiltration Florida
Orange County Water District, CA, USA
Notes: 32

## Slide 33
Typical RO/NF Process Control
Feed
Concentrate
Permeate
VFD
FIT
FIT
Concentrate Flow
Control Valve
RO Feed Pump
With VFD

## Slide 34: Membrane Terminology - Flux
Flux = Flow rate through a given membrane area
Essentially the production rating of a membrane
400 ft2
4800 gpd
Flux = 4800 gallons per day per 400 ft2
= 12 g/ft2/d (sometimes abbreviated GFD)
(In metric countries L/h/m2 or LMH)

## Slide 35
Ratio of the permeate flow to the feed flow
as %
Flow
Feed
Flow
Permeate
Recovery
=
Permeate Flow
VFD
RO Feed Pump
With VFD
Water
Concentrate Flow
Feed Feed
Membrane Terminology – Recovery
Courtesy Separation Processes Inc

## Slide 36
Membrane Terminology - Rejection
The percentage of Total Dissolved Solids (TDS) that does not pass through the membrane, based on the TDS concentration in the feed water.
Permeate TDS
VFD
RO Feed Pump
With VFD
Salt
Concentrate TDS
Feed TDS
Courtesy Separation Processes Inc.

## Slide 37: RO Example of Rejection %
Feed Permeate Rejection* mg/L mg/L %
Ca 2+
Mg 2+
Na +
NH4+ (as N)
Cl -
HCO3-
SO42-
TOC
SiO2
Total Nitrogen (as N)
TDS
* System Rejection: 10gfd @ 85% Recovery
32.9
19.4
134
26
147
130
197
11
22
27.4
600
0.034
0.015
3.44
0.91
2.2
7.7
< 2.0
0.2
0.14
0.9 26
99.9%
99.9%
97.4%
96.5%
98.5%
94.1%
> 99.0%
98.2%
99.4%
96.7%
95.7%

## Slide 38: Membrane Terminology
1st Pass, 2 stages
 | Stage | Pass
Definition | One step in sequential concentration | Passage through a membrane
Flow path | Concentrate from one stage feeds the next | Permeate from one pass feed the next
2nd Pass, 1 stage

## Slide 39
Concentrate
Example – A Three-Stage RO Unit
First stage vessel
Second stage vessel
1
2
3
4
5
1
2
3
4
5
5
4
3
2
1
Feed
Pump
1
2
3
4
5
Permeate
Third stage vessel
1
2
3
4
5
5
4
3
2
1
Courtesy Separation Processes Inc.
Notes: 39

## Slide 40: The RO Unit Design
RO unit configuration designed using specialist software supplied by vendors
Courtesy: Dow

## Slide 41: RO System Components

## Slide 42: RO Membranes – An Effective Depth Filter
Good pretreatment selection is essential
1000 mm
6000 mm
An effective depth filter
Particulate fouling often remains and is difficult to remove

## Slide 43: Silt Density Index (SDI)
A calculated number based on filtration of a sample through a 0.45 micron filter pad. SDI readings are used to indicate the “fouling” tendency of a water for use as RO feedwater.
SDI is calculated by following formula:
100 (1 – T1/T2)
SDI15 = 15
Where T1 is time in seconds to filter initial 500 ml
T2 is time in seconds to filter final 500 ml
Start taking 2nd sample after 15 mins
Courtesy Separation Processes Inc.

## Slide 44: Pre-Treatment Requirements
Cartridge Filters (5-40 micron)
  Typically used on ground water
    SDI feed water 3-5
    SDI product < 3
Media Filters (conventional or direct)
  Some surface waters
  Some groundwaters (where Iron & aluminium removal required)
  Seawater desalination
    SDI Feedwater > 6
Membrane Filtration
  Water reuse – should be < 3 to maintain RO warranty in reuse applications
  Seawater
    SDI Feedwater > 6

## Slide 45: Scaling and Fouling of RO Membranes
Scaling – A chemical “scale” similar to what occurs in a water heater or boiler
    Generally occurs at back end of RO system – last few elements.
Fouling – More generic term
    Suspended solids, colloids, microorganisms, and organic chemicals
    Can occur at front end (lead elements) or back end or overall
Both scaling and fouling effect permeate flow, pressure and can effect permeate quality

## Slide 46: Scaling
Main culprits
Alkaline scales: CaCO3 / Mg(OH)2
Non-alkaline: CaSO4
Sparingly soluble: BaSO4/SrSO4/CaF2
Silica (gel & colloidal)
Ca3(PO4)2 – (Water Reuse)
Control techniques
Antiscalant (threshold inhibitor)
pH Control (usually acid dosing)
Limit maximum recovery

## Slide 47: Anti-scalant (Threshold Inhibitor)
  Inhibits Precipitation of sparingly soluble salts in the RO concentrate stream
    Calcium Carbonate (CaCO3)
    Calcium Sulfate (CaSO4)
    Barium Sulfate (BaSO4)
    Silica (SiO2)
Notes: (If a crystal does not reach its critical mass, it will re-dissolve into solution).
Mechanism of Antiscalant:
1. Threshold Inhibition (Antiscalant adsorbs onto crystal seeds just as they start to form and acts as a barrier from other ions to prevent development of crystal growth. The crystal seed never reaches its critical mass and easily re-dissolves and this puts the antiscalant back in solution)
2. Crystal Growth Modification (Antiscalant interferes with crystal growth resulting in imperfect structures. These distorted crystals are a less stable crystalline form of the same chemical compound and will therefore easily re-dissolve)
3. Dispersion (Antiscalant deposits on formed crystals and the Anionic charge of the antiscalant repels the crystals from each other, preventing them from coagulating and fusing into larger crystals. Antiscalant deposits on formed crystals and the Anionic charge of the antiscalant repels the crystals from each other, preventing them from coagulating and fusing into larger crystals).
4. Metal Ion Stabilization (By competing for the metal cation, the antiscalant delays the formation of insoluble salts)

## Slide 48: RO Membranes – Biological Fouling
Microorganisms accumulate on membrane surface
Extracellular polymers facilitates cake consolidation
Chloramine useful in wastewater reuse applications to prevent or minimize biofouling
  Biofilm limits mixing at RO surface
    More concentration polarisation (increased pressure)
    High local concentration of salts (increased transmission/less retention)

## Slide 49: Concentration Polarisation Membrane Surface Concentration > Brine Concentration
Permeate
Concentrate/Brine
Feed
Brine Spacer
Minimum
Flow
Increasing
Conc.

## Slide 50: Where Does the Fouling Occur in a RO System? (For example a 3-stage system)
Courtesy: Tony Fane
Flux
Concentration
Scale (CaCO3, Silica)
Biofouling
Particle colloids & Metal Oxides (Fe, Mn)

## Slide 51: Important RO Monitoring
Overall permeability/fouling
Removal of Salt
Fouling in the brine channel

## Slide 52: RO Cleaning
Types of Cleaning Solution
High pH for organic/biological fouling
Detergents
Low pH (often citric acid) for scaling compounds
Specialist cleaners for difficult fouling (for example silica)
Courtesy Dow Technical Manual www.dow.com
Cleaning System – Signal Hill California
Know the foulant to target the clean
Cleaning Process
Cleaning is a recirculation on the feed to concentrate side of the membrane
Small amount of permeate produced – must be recirculated to avoid backpressure to membranes

## Slide 53: Permeate Backpressure
Restricting the permeate flow by closing a valve is detrimental to the membranes
This will cause delamination and render the membranes useless
Hence, RO systems cannot be backwashed

## Slide 54: Permeate Backpressure
Closed Permeate Valve
Back flow causing delamination
P~<10
Pressure drop in permit is proportional to hydraulic losses in the Feed/Brine Channel and the permeate side
Once the pressure equalizes, the perm. pressure at the tail is higher than the Feed/Brine – forcing flow in reverse
Water is incompressible

## Slide 55
Identify fouling
Identify damage/loss of rejection
Visual review of condition
Membrane Autopsy – Troubleshooting Tool

## Slide 56: Chloramine for Biological Fouling

## Slide 57: The Scourge of Biological Fouling
There is a catch!
Effluent is highly biologically active

## Slide 58: Biological Fouling Impacts
Fouling blocks feed-brine channel
Increased energy, increased cleaning costs

## Slide 59: Using Chloramine Can Assist with Biology
100
150
200
250
0
10
20
30
0
5
10
15
20
25
Transmembrane
pressure (psi)
0 ppm as Cl2
3 ppm as Cl2
0 ppm as Cl2
3 ppm as Cl2
Reverse Osmosis
Microfiltration
Days
Orange County Water District – Water Factory 21 Pilot Testing
Chloramine application slows the increase in transmembrane pressure and decreases cleaning cycles
Other biocides are available, but chloramine is very inexpensive.

## Slide 60: Use of Chloramines So Far

## Slide 61: Decades of Chloramine for RO Orange County – Water Factory 21 -1976
Cl2
Cellulose Acetate RO Membranes
Tolerant to Free Chlorine

## Slide 62: Studies on Use of Chlorine – 1984 (Ridgway et al , Journal AWWA, 1984)
Chlorine used to control fouling
Testing conducted at different chlorine doses
Low – 1 – 3 mg/L as Cl2
High 15-20 mg/L as Cl2

## Slide 63: Eraring, NSW Australia 1994
Polypropylene MF – not chlorine compatible
Chlorine dosed upstream of RO
RO operated > 1 year without cleaning
Cellulose Acetate RO Membranes
First Use of MF together with RO for Reuse
Cl2

## Slide 64: The Move from CA to TFC Membranes
Improvements in membrane chemistry resulted in significant power savings for water reuse applications
1976 (CA)
0.0
2.0
4.0
6.0
0
150
300
450
600
Pressure (psi)
Energy Usage (kWh/1000 gallons)
1980 (TFC)
1990 (CA)
1994 (TFC)
1997 (TFC)
1995 (TFC)
Source: Water Factory 21 municipal wastewater reclamation plant

## Slide 65: Thin Film Composite Polyamide Have Multiple Layers…
FABRIC
0.1 micron Polyamide
75 micron Polysulfone
2000 micron Polyester Fabric
Polyamide

## Slide 66: …But – Poor Tolerance to Free Chlorine
11 years at 3ppm
2 weeks at 3 ppm
300,000 ppm hours
1000 ppm hours
Based on a typical membrane supplier recommendation

## Slide 67: TFC Membranes Are Compatible with Chloramine But Inconsistencies Exist in Supplier Warranties
RO Membrane 1 | Maximum Tolerable Chloramine Concentration
Membrane 1 | Up to 5 mg/L as Cl2
Membrane 2 | Up to 3 mg/L as Cl2
Membrane 3 | Less than 2 mg/L as Cl2
Different vendors have different levels of experience with chloramine
Different membrane elements have different surface membrane coating thicknesses
Different warranty requirements (e.g. tighter quality specification)

## Slide 68: How Much is Enough?
We must balance the amount of chloramine allowable to prevent significant membrane damage while also providing sufficient to minimize biological growth.
Too little (< 3 mg/L) chloramine will not be effective.
McVay, Florida Rural Water Association

## Slide 69: Managing the Chloramine Dose

## Slide 70: Chloramines
Formed by combining ammonia and free chlorine
  NH3 + HOCl  H2O + NH2Cl (monochloramine)
  NH2Cl + HOCl  H2O + NHCl2 (dichloramine)
  NHCl2 + HOCl  H2O + NCl3 (trichloramine)
Monochloramine predominant at pH > 7
  Most favorable conditions
    pH range of 7.5 to 9.3
    Chlorine:Ammonia ratio 3:1 to 4:1
Much weaker disinfectant than HOCl (or OCl-)

## Slide 71: Breakpoint Chlorination: Residual Doesn’t Indicate if Mono or Dichloramine
Want to target a chlorine to ammonia ratio of 4:1
Notes: As we know, the Stage 2 D/DBP Rule developed by the USEPA and promulgated on January 4 2006 builds upon regulatory requirements for total trihalomethanes (TTHM) first promulgated in 1979, and more stringent TTHM and haloacetic acid (HAA) limits which became effective in January 2002 under the Stage 1 D/DBP Rule. \
The Stage 2 Rule has been put in place to limit the maximum concentrations of Disinfection By-Products reaching consumer taps. It is more stringent than the Stage 1 Rule in that it attempts to provide more equitable public health protection.
For systems coordinating compliance with the Stage 2 Rule, several options are available and fall into the categories of limiting organic precursor material prior to disinfection and/or switching disinfectant.
Typically, organic precursor material is removed from source water through filtration and adjustment of filtration practices at some utilities may improve removal of DBP precursors, namely organic carbon. However, there are some new technologies, such as MIEX that can assist in removal with or without corresponding filtration.
The typical way to lower TTHM and HAA5 concentrations through disinfection is to disinfect with mono-chloramine instead of chlorine. Again, other disinfectants exist but these two are used most routinely in drinking water treatment.

## Slide 72: Distribution of Chloramine Species with pH
(2.5mg/Chlorine; 0.5 mg/L ammonia-nitrogen: temperature 25OC; contact time 2 hours)
Typical RO Feed pH
Typical RO Permeate
Driver for low pH is scaling control
Lower pH may lead to dichloramine formation
Dichloramine is stronger oxidant
  May also form DBPs such as NDMA

## Slide 73: Dosing Control Approaches
ORP
Cl2
pH
In this case, the wastewater does not contain sufficient ammonia and some must be added. In some cases, where ammonia is not specifically targeted for wastewater treatment, there is sufficient ammonia already in the wastewater and additional is not required.

## Slide 74: Dosing Control
Total chlorine provides useful information
Free chlorine (DPD method) false +ve interferences)
Free chlorine – relying on zero reading – may not be as effective
Chloramine analyzers show promise, but have high maintenance requirements
Monitoring presences of ammonia guarantees that chloramine has not reached breakpoint hence chlorine is in the chloramine form
Cl2
Courtesy – Western Corridor Recycled Water Project

## Slide 75: How to Provide a Stable, Controlled Dose
It is important to first understand the wastewater chlorine demand – what will be consumed by organics/chlorine demand?
Wastewater quality can fluctuate seasonally and diurnally
Precise control not possible, and is not necessary
+/- 0.5 mg/L or more is acceptable
Ammonia may also fluctuate in the feed, important to monitor.
Courtesy – Western Corridor Recycled Water Project

## Slide 76: Different Ammonia Levels in Wastewater
Minimal nitrification – ammonia present
Fully nitrified wastewater
No reliable ammonia level
Ammonia dose required
Courtesy Western Corridor Recycled Water Project
Owens et al, AWWA MTC 2015.

## Slide 77: Dosing Control – ORP
ORP analyzers can drift and require regular calibration
Jar testing or measurement of actual ORP when chlorine is overdosed can be useful in providing alarm set points
A rate of change alarm (rate of change in ORP) is also a useful way of identifying a free chlorine breakthrough event
ORP
Steinenger et al, NSPI Symposium Series, Vol. I (1996)
Hach Company, Loveland Ohio
We need a method of protecting the membranes from free chlorine. This may occur if ammonia levels drop or ammonia dosing fails. ORP will increase significantly if free chlorine is present.

## Slide 78: Dosing Control – Control Response ORP
Often the control response is rapid RO shutdown
However in this case, chlorine will be contacting the membranes
Permeate flush will also introduce chlorine to the membranes as chlorine is not well rejected by the RO
The best approach is to continue operating and stop chlorine, or stop chlorine in the feed and flush with unchlorinated feed water until the chlorine has been displaced
Courtesy – Kwinana Water Reclamation Plant, Australia

## Slide 79: Checking the Membrane Condition

## Slide 80: Are Membranes Oxidized?
The Fujiwara test is a common diagnostic test used in membrane autopsy, however there are some doubts on its reliability
It detects halogenation on the polyamide membrane layer with a color detection test (pictured)
Some membranes are chlorinated during manufacture, and will as a result always provide a positive test for chlorine on the Fujiwara
Courtesy Avista Technologies.
Fujiwara Halogenation Test
Gabelich et al, Journal of Membrane Science 258 (2005)

## Slide 81: Are Membranes Oxidized ?
Monitoring RO membrane rejection using normalized data is important to determine any sudden impact from chlorine damage. Chloramine will decrease rejection over time, however this is balanced against the ability to manage biofouling.
Courtesy, Western Corridor Recycled Water Project

## Slide 82: The Presence of Iron and Aluminum Can Catalyse an Oxidation Reaction
Fe (II) and Al catalyze amidogen
Amidogen radical thought to expose polyamide ring to direct chlorine attack from chloramine
Gabelich et al, Journal of Membrane Science 258 (2005)
H
H
N
Cran et al, Institute of Sustainability Victoria.
Amidogen radical

## Slide 83: Unintended Consequences

## Slide 84: Unwanted Byproduct Formation
Chloramine can form unwanted byproducts.
Preformed
Direct Dose
Courtesy – Western Corridor Recycled Water Project - 2008

## Slide 85: Dosing Approaches to Minimize Byproducts
An option if ammonia added
Ammonia
Chlorine
To MF/RO
Effluent
Ammonia
Chlorine
To MF/RO
RO Permeate Carrier Water Stream
Effluent
Direct Dose
Pre-formed Dose

## Slide 86: Chloramine Passes Through the RO
Chart: Chlorine Data Orange County RO System
Courtesy – Orange County Water District
Chloramine passes through to the permeate. We need to take this into account for final disinfection (break point with additional chlorine will be required). When advanced oxidation, or UV disinfection is used downstream of RO, the chloramine will lower UVT and increase energy demands.

## Slide 87: Chloramine Dosing – A Critical Control Point
NDMA Control
Microorganisms
Microorganisms
Chemicals of Concern
Microorganisms
Chemicals of Concern
Lead/copper leaching in distribution system
Micro-organisms
Notes: As a part of a project with WRRF identifying and using critical control points, the following have been identified including:
Microfiltration as a barrier to microorganisms.
Reverse osmosis as a barrier to microorganisms and dissolved chemicals of concern.
Advanced oxidation for both microorganisms (Via UV) and specific chemicals of concern.
Chlorine dosing for a CT for microorganisms.
Additionally, chloramine dosing, used as a preventative measure to avoid biological fouling on RO, qualifies as a critical control point as it has the potential to introduce a risk which must be managed.
Also, stabilization has been identified as a CCP. Reverse osmosis produces an aggressive water which if not stabilized, can lead to lead and copper leaching in distribution networks and home services.

## Slide 88: Impact on Advanced Oxidation Processes

## Slide 89: Impact to Advanced Oxidation

## Slide 90: AOP – Increased Energy Requirement
Omerci, Ishida, Linden
Chloramine reduces UV transmittance, increases power requirement.

## Slide 91: AOP – Increased Hydrogen Peroxide Dose
0.5 mg/L of H202 for every 1 mg/L Cl2
Additional peroxide is required to quench chloramine residual in RO permeate when peroxide advanced oxidation is used

## Slide 92: Environmental Issues
Chloramine will exist in the RO concentrate stream
Environmental impacts depending on discharge
Removal may be required
Nitrification
Denitrification
Courtesy, Western Corridor Recycled Water Project

## Slide 93: O-Ring Oxidation
Recommend peroxide cured EPDM

## Slide 94: Conclusions
Chloramine inexpensive, effective biocide
Careful design of dosing system required
Control strategies critical
Careful attention to downstream water quality
Has impacts on advanced oxidation processes
Has impacts on plant equipment

## Slide 95: Critical Control Response Procedures

## Slide 96: Hazard Analysis and Critical Control Point (HACCP) History
Systematic preventative approach to Food Safety
Focus on barriers – not end of pipe treatment
Adapted to IPR and DPR through projects WRRF-09-03 and Reuse-13-03
Conceived in 1960s by Pillsbury for NASA
Defined in ISO 22000 – Food Safety

## Slide 97: Critical Control Points (CCPs) Defined
CCPs are points in the treatment process that are specifically designed to reduce, prevent, or eliminate a human health hazard and for which controls exist to ensure the proper performance of that process.

## Slide 98: Example Critical Control Point – RO
Risk: Chemicals of concern and microorganisms
EC
Monitor validates the barrier
If monitor detects barrier not intact then control action and standard operator response
Notes: Using the example of reverse osmosis. The critical control is monitored by a monitor that will detect if the barrier is not intact. In this situation, usually the automated control system will shut down that portion of the process until the situation can be rectified.

## Slide 99: Chloramine Alert (Warning) Response

## Slide 100: Chloramine Dosing Critical Alarm (Failure) Response

## Slide 101: RO Alert (Warning) Response

## Slide 102: RO Critical Alarm (Failure) Response

## Slide 103: Additional Design Criteria

## Slide 104: RO Design Criteria
Design criteria for RO and NF is included in the existing training material provided by membrane organizations (as noted later in this module)
Additional considerations that should be considered for IPR/DPR systems include:
Dissolved Total Organic Carbon Monitoring
Alternative integrity/log removal monitoring approaches

## Slide 105: On Line TOC
On Line total organic carbon (TOC) analyzers can measure low levels of organic carbon in RO permeate (in the 10 – 50 ug/L range).
TOC measured upstream of the RO, and in the RO permeate can provide an indication of overall membrane integrity to a higher resolution than electrical conductivity (greater than 2 log).
A spike in permeate TOC may also indicated a higher concentration of low molecular weight, non-polar material in the RO feed. It can be used as a trigger to investigate for a spill of industrial material into the sewer catchment. It can also trigger based on plant issues, including leaching of material from new tank liner material.
Online TOC analyzers are expensive, and consequently typically used on a combined RO permeate stream.
Courtesy GE

## Slide 106: Alternative Integrity Monitoring
Alternative monitoring approaches are currently under development for improved monitoring of RO membrane integrity. This is to advance the log removal that can be validated beyond the current limitation of 1.5 to 2.0.
These are often a dose of chemical with a marker type compound such as rhodamine, uranine or other proprietary chemical. These are either dosed as a separate inlet dose to the RO unit, or incorporated into the antiscalant dose.
Monitoring techniques vary depending on the chemical used.

## Slide 107: Process Components

## Slide 108: Process Components
This material is covered in existing training course noted later in this module

## Slide 109: Operation and Maintenance

## Slide 110: Operation and Maintenance
O&M items are included in the existing training material noted later in this module

## Slide 111: Safety

## Slide 112: RO Safety Concerns
As with any operating process, there are safety concerns associated with RO
High Pressure – RO units operate at higher pressure. Operators must take care to understand what points on the RO are at high pressure.
Corrosive Chemicals – RO cleaning requires both caustic and acid chemicals for cleaning. Operators must take care with handling of chemicals during RO cleaning.
Manual Handling – Careful consideration of RO membrane loading and unloading is important. Membranes may be located at high points and at loading and unloading safe access to pressure vessels is important.

## Slide 113: Introduction to RO Processes (South East Desalting Association – Handbook for Membrane Plant Operator Training Module 1)

## Slide 114: Module 1 – Handbook for Membrane Plant Operator Training
Chapter 1 – Introduction to Membrane Processes
1.00 Introduction
1.01 Water Permeable Membranes
1.02 Membrane Types and Materials
1.03 Permeable Membrane – Configurations
1.04 Tubular and Plate and Frame Configurations
1.05 Spiral Wound Configuration
1.07 Hollow Fiber Straight Through Configuration
1.08 Historical Review – Permeable Membranes
1.10 Water Impervious Membranes

## Slide 115: Module 1 – Handbook for Membrane Plant Operator Training
Chapter 2 – Reverse Osmosis Membrane Processes
2.00 Introduction
2.10 Basic Principles (What is Osmosis?)
2.20 Flow Across the Membrane
2.30 Basic RO Systems
2.40 Element Construction
2.50 Fouling, Damage, Cleaning and Troubleshooting RO Systems
2.60 What Can RO Do and What Can RO Not Do

## Slide 116: Introduction to RO Processes (South East Desalting Association – Handbook for Membrane Plant Operator Training Module 2)

## Slide 117: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 10 – Pre-Treatment Chemicals
10.00 Introduction
10.01 Basic Principles
10.11 Why Feed Pretreatment Chemicals?
10.12 Definition of Fouling/scale
10.13 Definition of Scale Inhibitor/Antifoulant
10.14 How Scale Inhibitors Work
10.15 How antifoulants Work
10.20 History of Inhibitors in Membrane Treatment
10.21 Sodium Hexametaphosphate
10.22 Polyacrylate
10.23 HEDP
10.24 Organic co-polymers and terpolymers

## Slide 118: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 10 – Pre-Treatment Chemicals (Continued)
10.30 Product and dosing recommendations
  10.31 Product and dosage recommendations by supplier computer software
  10.32 Pilot Test Skids
  10.33 Plant scale testing
10.40 Proper Feed Methods
  10.41 Where to feed the product
  10.42 Consequences of chemical underfeed or overfeed
  10.43 Determining if feed rate is correct
  10.44 Dilution of scale inhibitor/antifoulant

## Slide 119: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 11 – Pre-Treatment Filtration
11.00 Introduction
11.10 Defining Filtration
11.20 Selecting the Proper Pre filtration
11.30 Cartridge Filters
11.31 Cartridge Filter Materials
11.32 Wound Polypropylene
11.33 Pleated Polypropylene
11.34 Melt Blown (Depth)
11.35 Spun Bonded
11.36 Bi-component
11.40 Cartridge Filter Rating and Efficiency
11.41 Efficiency
11.42 Beta Ratio
11.50 Cartridge Filter Vessels
11.51 Initial Installation for New Vessels
11.52 Cover Replacement and Start Up
11.53 Shutdown and Cartridge Change Procedure
11.54 Troubleshooting

## Slide 120: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 11 – Pre-Treatment Filtration (continued)
11.60 SDI Procedure
11.70 Media Filters
11.80 Centrifugal Sand Separators
11.90 Automatic Self Cleaning Strainers
11.91 Multi Tubular Type
11.92 Stationary Drum Type With Rotating Backwash Arm
11.93 Rotating Drum with Stationary Backwash
11.94 Expandable Disc

## Slide 121: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 12 – Membrane Applications
12.00 Introduction
12.10 RO System Design
  12.11 Flux
  12.12 Trans Membrane Pressure
  12.13 Recovery Rates
  12.14 Concentration Factor
  12.15 Membrane Arrangements
  12.16 System Control
12.20 Seawater RO
12.30 Brackish RO
12.40 Nanofiltration

## Slide 122: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 13 – Operating Membrane Systems
13.00 Introduction
13.10 Initial Start UP
  13.11 Pre-start up check
  13.12 Initial pre-start up checklist
  13.13 Startup sequence
13.20 Normal Operation Start Up
13.30 Normal Operation Shut Down
13.40 Adjustment of Operational Parameters
13.50 Maintenance Log
13.60 Conductivity Profile
13.70 Control of Microbiological Activity

## Slide 123: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 14 – Data Collection and Normalization
14.10 Record Keeping
14.20 Record Keeping Plan
14.30 Chemical Analyses
14.40 Normalization of RO Performance
14.50 Normalization Equations
  14.51 Salt Passage
  14.52 Normalized Differential Pressure
  14.53 Normalized Permeate Flowrate
  14.54 Example Case
14.60 Graphing Normalized Data

## Slide 124: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 15 – Troubleshooting
15.00 Introduction
15.10 Instrumentation
15.20 Changing Conditions
15.30 Silt Density Index
15.40 “O” Rings and Profiles
15.50 Damaged Membrane
15.60 Fouled or Scaled Membrane

## Slide 125: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 16 – Membrane Cleaning
16.10 Fouling
  16.11 Turbulence
  16.12 Concentration Polarization
  16.13 Chemical Fouling and Scaling
  16.14 Raw Water Supply and Pretreatment
  16.15 Bacteria and Organic Debris
16.20 When to Clean
16.30 Chemical Cleaners
16.40 Chemical Fouling Removal
16.50 Colloidal Fouling Removal
16.60 Biological Fouling Removal
16.70 Monitoring the Cleaning Cycle
16.80 Cleaning System Equipment

## Slide 126: Module 2 – Handbook for Membrane Plant Operator Training
Chapter 17 – Concentrate Disposal
17.00 Introduction
17.10 Concentrate Disposal Methods
  17.11 Surface Water Discharge
  17.12 Injection Well Discharge
  17.13 Other Discharge Methods
17.20 Treatment of Concentrate Streams

## Slide 127
The Water Research Foundation (WRF) is a nonprofit (501c3) organization which provides a unified source for One Water research and a strong presence in relationships with partner organizations, government and regulatory agencies, and Congress. The foundation conducts research in all areas of drinking water, wastewater, stormwater, and water reuse. The Water Research Foundation’s research portfolio is valued at over $700 million.
The Foundation plays an important role in the translation and dissemination of applied research, technology demonstration, and education, through creation of research-based educational tools and technology exchange opportunities. WRF serves as a leader and model for collaboration across the water industry and its materials are used to inform policymakers and the public on the science, economic value, and environmental benefits of using and recovering resources found in water, as well as the feasibility of implementing new technologies.
For more information, contact:
The Water Research Foundation
Alexandria, VA Office
1199 North Fairfax Street, Suite 900
Alexandria, VA 22314-1445
Tel: 571.384.2100
www.werf.org werf@werf.org
Denver, CO Office
6666 West Quincy Avenue
Denver, Colorado 80235-3098
Tel: 303.347.6100
www.waterrf.org Info@WaterRF.org
© Copyright 2018 by The Water Research Foundation. All rights reserved. Permission to copy must be obtained from The Water Research Foundation.
WRF ISBN: 978-1-60573-363-0
WRF Project Number: Reuse-15-05/4772
This report was prepared by the organization(s) named below as an account of work sponsored by The Water Research Foundation. Neither The Water Research Foundation, members of The Water Research Foundation, the organization(s) named below, nor any person acting on their behalf: (a) makes any warranty, express or implied, with respect to the use of any information, apparatus, method, or process disclosed in this report or that such use may not infringe on privately owned rights; or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of, any information, apparatus, method, or process disclosed in this report.
Hazen and Sawyer, Carollo Engineers Inc., Santa Clara Valley Water District
This document was reviewed by a panel of independent experts selected by The Water Research Foundation. Mention of trade names or commercial products or services does not constitute endorsement or recommendations for use. Similarly, omission of products or trade names indicates nothing concerning The Water Research Foundation's positions regarding product effectiveness or applicability.