## Slide 1: Ozone Disinfection Module

## Slide 2: Project Partners
Hazen and Sawyer
Carollo
Santa Clara Valley Water District
LA Sanitation District
Gwinnett County (GA)
El Paso Water Utilities
UFTREEO (University of Florida)
Sacramento State
University of Arizona-WEST Center
TrojanUV
Xylem Inc.
Process Applications Inc.

## Slide 3: Module Outline
Definition of ozone
The role of ozone in potable reuse
Ozone reactions in water
Ozone equipment
Ozone dosing and control
Operation, monitoring, and maintenance priorities for an ozone system
Critical monitoring and response procedures
Ozone safety

## Slide 4: Process Overview and Introduction
Definition of ozone
Role of ozone in potable reuse
Ozone reactions in water

## Slide 5: Ozone Definition
Ozone (O3) is formed when oxygen molecules are exposed to electron flow
Ozone molecules are unstable and will lose third oxygen atom over time

## Slide 6: Ozone Formation
Ozone is formed by
  Ozone generators provide electron flow within a narrow gap (~0.5mm) between dielectric & SS tube
  Oxygen is passed through the gap, resulting in ozone generation
  Important: oxygen feed gas must be dry and free of particles
  Important: ozone generators must be cooled, cooling water removes >90% of heat
Type shown is corona discharge ozone generating cell
High Voltage AC Source
++++++++++++
------------------

## Slide 7: Potable Water Reuse Requires Multiple Barriers for Reliable Purification
Target | WWTP | UF | RO | UV/AOP
Protozoa | X | X | X | X
Virus | X |  | X | X
MCLs | X |  | X | X
CECs | X |  | X | X
Target | WWTP | Ozone | BAF | UF | GAC | UV/AOP
Protozoa | X | X | X | X |  | X
Virus | X | X |  | X |  | X
MCLs | X | X | X |  | X | X
CECs | X | X | X |  | X | X
Ozone Provides Destruction of Pathogens and Chemical Pollutants

## Slide 8: For Some Projects, O₃ is Coupled with RO-based Treatment
Ozone
Biologically
Active
Filtration
Ultrafiltration
Reverse Osmosis
Ultraviolet Disinfection Advanced Oxidation
Photo: San Diego California Permanent Potable Reuse Demonstration System
Secondary or Tertiary Effluent

## Slide 9: Ozone is a Critical Process for Non-RO Purification – Shown Here Coupled with BAF
Ozone
Biologically
Active
Filtration
Ultrafiltration
Granular Activated Carbon
Ultraviolet Disinfection
Photos: Altamonte Springs FL Permanent Direct Potable Reuse Demonstration System
Secondary or Tertiary Effluent
Virus kill
Protozoa removal
TOC reduction
Trace chemical pollutant reduction

## Slide 10: Summary of Ozone Values
An oxidation process used as microorganism inactivation process and oxidation prior to BAC
Floc aid
Organic contaminant destruction
Inactivation of Virus, Bacteria, and Protozoa

## Slide 11: Oxidation by Hydroxyl Radical (OH*)
Hydroxyl radicals (OH.) are formed during initial dissolution in water and continue to form as ozone residual decays in the contactor (Addition of hydrogen peroxide (H2O2) accelerates conversion of O3 to OH.. This is called advanced oxidation process, AOP)
Very powerful oxidant, extremely reactive, non-selective, short lived (~10µs), and very difficult to measure
Alters charge and may improve settling of particles (micro-coagulation) resulting in lower settled water and filtered water turbidity
Hydroxyl radical destroys complex organics
  T&O compounds including 2-methylisoborneal (MIB) & Geosmin
  Pesticides
  Organic solvents (TCE & PCE)
  Pharmaceuticals and personal care products (PPCPs)
  Potential Endocrine disrupting compounds

## Slide 12: Oxidation by O3 Residual and OH*
OH is formed when ozone is applied to water
Amount of OH. formed depends on
  pH Higher pH = more OH.
  TOC Higher TOC = more OH.
  Temperature Higher Temperature = more OH.
  Alkalinity Lower alkalinity = more OH.
These two reactions are important because disinfection and destruction of chemical pollutants occurs at different rates and with different effectiveness depending upon the reaction

## Slide 13: Balancing Disinfection and Oxidation for Operations: Pros and Cons of OH. and O3
Item | Ozone | Hydroxyl Radical
Residual | Ozone can be overdosed beyond demand to create a short-lived residual | Residual impossible, hydroxyl radical half-life is too fast
Reaction with Inorganic Compounds | More reactive due to longer exposure time. Forms some unwanted chemicals, such as bromate (from bromide) | Much less reactive with inorganic compounds
Reaction with double-bonded chemicals | Less effective oxidant | More effective oxidant
Disinfection | Ozone residual proven and granted credits for virus and protozoa. Also effective against bacteria. | Wastewater validation work in California demonstrates kill of virus and bacteria, but not protozoa
Total Organic Carbon | Effective oxidant | Highly effective oxidant

## Slide 14: Disinfection Terminology
Disinfection
The action of killing or inactivating disease causing micro-organisms, which are called pathogens
Microorganism
A small creature visible by a microscope
Water Regulated pathogens: Virus; Giardia; Cryptosporidium
  Inactivated by exposure to ozone residual and time (CT, Concentration multiplied by contact time)
  Virus inactivated based upon Ozone/TOC ratios properly adjusted for nitrite concentrations
Wastewater Regulated Pathogens: Fecal Coliform; E. coli; enterococci
  Inactivated by exposure to ozone residual and time (CT)
  Bacteria inactivated based upon Ozone/TOC ratios properly adjusted for nitrite concentrations
Log Inactivation: also can be called “%kill”
1-log = 90%; 2-log = 99%, 3-log = 99.9%

## Slide 15: Ozone Disinfection of Wastewater
Inactivation of fecal coliform occurs due to reactions with both ozone residual and OH. during the initial demand phase when ozone is applied and during the ozone residual decay phase when CT can be measured
Ozone residual is easier to measure than OH. and immediate feedback of overall exposure is measured as CT (residual times time)
Ozone residual develops after ozone demand is met but decays quickly
Sampling locations early in the contactor are required to measure residual before it decays

## Slide 16: Ozone Demand and Decay
Ozone demand is the difference between transferred ozone dose and initial residual
If first sample point is located several minutes downstream, apparent ozone demand will be greater than true demand because of ozone decay
Ozone decay rate may be used to calculate residual values upstream or downstream of sample points
0.0
0.2
0.4
0.6
0.8
1.0
1.2
1.4
1.6
1.8
2.0
0
1
2
3
4
5
6
7
8
9
10
Time, minutes
See Legend
Ozone Residual, mg/L
Apparent Ozone “Demand”, mg/L
First order decay is established after initial reactions.

## Slide 17: Nitrite Reaction with Ozone
One mole of NO2- (46 gm/mole) reacts with one mole of O3 (48 gm/mole)
This means that 1 mg/L of nitrite will immediately consume ~1 mg/L of ozone
Treated wastewater might contain nitrite, which will increase ozone demand

## Slide 18: By-Products of Ozone Oxidation
Bromate
  Regulated bromate limit is 10µg/L (running annual average)
  Ozone oxidizes bromide, forming bromate
    Bromate well removed by RO
    Bromate can be minimized by keeping O₃/TOC ratio low (often <1) and not making an ozone residual
    pH reduction and ammonia-chlorine processes can also minimize bromate
    Critical to understand bromate concentrations based upon site-specific data at this time

## Slide 19: Ozone System Equipment and Generation
Equipment to produce and apply ozone to water

## Slide 20: Major Components of Ozone System
Gas to atmosphere

## Slide 21: How Dry is “Dry”?

## Slide 22: Schematic of a LOX-fed Ozone System
Ozone contactor
Vents to atmosphere
Water chiller
Water chiller

## Slide 23: LOX Storage
Instruments
  Level
  Pressure
O&M Considerations
  Maintenance by LOX supplier
  Fill procedure
  Specify total hydrocarbon (THC) <25 ppm (AWWA B304-8 in process of update)
  Keep all tanks on line to minimize THC concentration due to boil-off

## Slide 24: Ambient Vaporizers
Fin tube heat exchangers
Vaporize liquid oxygen (LOX) to gaseous oxygen (GOX) and build pressure
Outlet GOX valves used to alternate vaporizers based on time with low temperature override
(Note that vaporizers should be alternated to avoid the same vaporizer having a recurrent defrost cycle at the same time of day. Best to cycle on 7,9,10, 11 or 13 hr periods.

## Slide 25: Oxygen Pressure Regulating Valve & Filter
Reduce and stabilize variable GOX pressure from vaporizers
High quality valve sized for full range of oxygen flow while maintaining very stable output pressure is required for good downstream gas flow control
Monitor dew point and alarm to protect generator from moisture contamination
Feed gas pressure and temperature measured to protect ozone generator from overpressure or low temperature
Pressure regulating valves
Particulate filters

## Slide 26: Nitrogen Feed System
Supplemental dried air (79% N2) is added to ensure enough N2 present for efficient ozone production
Electron flow “excites” nitrogen molecules which helps split oxygen molecules
N2 reduces ozone generator energy consumption by about 15%
This effect lasts for hours after N2 is shut off due to microscopic coating of the dielectrics and stainless steel)
Less than 1% nitrogen in feed gas flow as recommended by manufacturer.
Nitrogen leads to deposition of contaminants on the dielectrics

## Slide 27: Dew Point Monitor
Dew point sensor requires annual regeneration by manufacturer (need spare on hand)
Will fail to low temperature if not replaced and therefore will not provide adequate alarm if maintenance is ignored
Adequate Dew Point is a required permissive for ozone generator operation
Failure of instrument can result in higher moisture – potential for nitric acid formation

## Slide 28: Ozone Generator

## Slide 29: Ozone Generator, Simplified Diagram
Gas & electron flow in gap
Glass or ceramic dielectric
SS tube, (ground electrode)
Generator Shell
Power
Ozone (& oxygen) OUT
Oxygen IN
Cooling water OUT
Cooling water IN

## Slide 30: Optimizing Ozone Energy and LOX Cost
  Example Design Point
  10%wt, 780 lb/day, 4.5 kWh/lb, 146 kW
  Max production at other
  ozone concentrations
  12%wt, 660 lb/day, 5.5 kWh/lb, 146 kW
  8%wt, 920 lb/day, 3.8 kWh/lb, 146 kW
  6%wt, 1060 lb/day, 3.3 kWh/lb, 146 kW
Optimum range
Cost of ozone production includes energy and LOX cost.
In the example below for average energy cost of $0.11/kWh and LOX cost of $60/ton, cost of ozone production is minimized (~$0.72/lb) by operating between 8%wt and 11%wt.
Ozone generator production capacity is rated at design ozone concentration such as 10%wt. Actual generator capacity will vary depending on operating ozone concentration. Greater production is possible at lower ozone concentration but LOX cost increases.
Energy cost = $0.11/kWh, LOX cost = $0.25/100CF ($60/ton)

## Slide 31: Cooling Water – Closed Loop vs Open Systems
Cooling water necessary to dissipate heat from ozone generators
Closed loop systems provide better control over cooling water quality to reduce possibility of corrosion and leaks
Open loops can be prone to clogging from biological growth and inorganic precipitation
About 2oF increase (approach) over open-loop cooling water temperature
Slightly more cost and complexity but positive control over cooling water quality is important benefit

## Slide 32: Ozone Dose Systems: Fine Bubble vs Side Stream

## Slide 33: Ozone Dissolution and Contacting
Bubble Diffuser
Side Stream Injection
The side stream option is becoming more popular today
1. Maintenance is outside of the ozone contactor 2. More cost effective now with high-concentration ozone
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
o o
- - - -
Water
Ozone
Historically, the most common
ozone contacting option. Diffuser maintenance may be significant.
Ozone
Water Flow
G
L

## Slide 34: Fine Bubble Diffusion
Lower capital and operating cost than side stream injection
Requires water depth of about 20’ above diffusers for good transfer
Requires periodic gasket replacement and diffuser cleaning
Maintenance requires confined space entry
Checking bubble pattern

## Slide 35: Types of Sidestream Injection Systems
Sidestream “with degas” to minimize gas bubbles in the downstream contactor
  All ozone is transferred in the side stream
  Pumping power is greater
  More contactor options including pipeline or shallow
Sidestream “without degas” to minimize pumping power
  Some ozone is transferred in the side stream
  Additional transfer occurs in the contactor
  Pumping power is lower

## Slide 36: Sidestream with Degas
Used when all ozone must be transferred in the sidestream before remixing with the main stream
Selected when site conditions dictate, such as for pipeline contactor, shallow contactor, or when lower dissolved oxygen is required
Requires higher sidestream water flow, and energy cost for pumping

## Slide 37: Sidestream without Degas
Transfer of ozone in the sidestream AND in the contactor
Selected when possible to reduce SS pumping cost

## Slide 38: Preventative Maintenance and Troubleshooting

## Slide 39: Moisture and Nitric Acid Contamination
Generating ozone in the presence of nitrogen molecules creates “NOX”, most notably N2O5
NOX and water (vapor or liquid) forms nitric acid. H2O + N2O5 = 2HNO3
Maintaining dew point < -60°C (<6ppm) minimizes moisture and nitric acid formation
Once formed nitric acid does not evaporate
Nitric acid trapped in ozone gas pipe or generator will reduce generator efficiency, corrode stainless steel, attack valves and instruments, and convert ozone back to oxygen, a reaction that gives off heat

## Slide 40: Avoiding Moisture Entrapment in Ozone Gas Feed Line
Include detailed layout in design drawings
Gas pipe enters top of venturi
Check valve located in vertical above venturi
Shutoff valve, fail-close valve, and moisture separator located in vertical or horizontal (sloped to vertical) with no low points to trap moisture
Pressure sustaining valve is optional

## Slide 41: Keeping Ozone Generators Dry
Utilize conservative purging procedures
  Standard pre and post purge time ~5+ minutes
  Use longer purge times if generator off line for longer periods (weeks or months) or if opened for maintenance
  Pre and post purge not necessary if generator off for less than ~1 hour
  Vendor O&M manuals have more detail about recommended purge times
Keep generator pressurized with dry oxygen when offline in standby mode. (i.e. inlet gas valve open, outlet valve closed)
With good practices, 5 to 10 years of efficient generator operation may be achieved before generator and dielectric cleaning is required

## Slide 42: Off-Gas Destruct System
Purpose – Remove ozone off-gas from contactor head space, maintain negative pressure (~-4 in. H2O) in contactor head space, raise off-gas temperature by ~30ºF to prevent condensation on the catalyst media, convert off-gas ozone to oxygen, and remove water from low points in off-gas piping
Components – Heater, manganese dioxide catalyst pellets, and centrifugal blower

## Slide 43: Off-Gas Moisture Removal
Moisture might condense in off-gas piping
Pipe should be sloped to allow drainage back to contactor
Auto or manual drainage at low points

## Slide 44: Process Operations
Ozone dosing and control systems
Operation, monitoring, and maintenance priorities for an ozone system

## Slide 45: Ozone Reaction Chamber – Use Multiple Chambers

## Slide 46: Ozone Reaction Chamber - > 3 Consecutive Reaction Chambers

## Slide 47: F Wayne Hill WRC, Pre-Filtration and Post-Filtration Ozone Treatment
Post Ozonation provides disinfection

## Slide 48: F Wayne Hill WRC, Post-Ozone
Post-ozone treatment objective is disinfection of fecal coliform to meet permit limit ensuring less than 2 CFU/100 mL
Typical ozone dose is about 0.5 mg/L to 1.6 mg/L
Ozone dose control is challenging because influent and effluent fecal coliform measurements are delayed, required CT values are not developed, ozone decay is rapid, and sampling locations are limited

## Slide 49: F Wayne Hill WRC, Post-Ozone
S2
S1
POST-OZONE CONTACTOR
CROSS SECTION
DOWNFLOW TUBE
NEWS0
S2

## Slide 50: Ozone Residual Sampling Considerations
Sample inlet in main water flow stream at outlet of each contactor cell.
Minimize length of sample piping.
Multiple monitoring locations recommended however grouping analyzers to common instruments to minimize calibration and maintenance is recommended
Wire between sensor and instrument should be long enough to move sensor to several sample stations

## Slide 51: Ozone Process Optimization
Optimize ozone production
  Monitor mass cost ($/lb or $/Kg)
  Operate in optimum concentration range
  Equipment & instrument maintenance
Optimize ozone dose
  Monitor performance trends & dose
  Operate in target performance range
  Special studies to optimize # of contactors, residual measuring locations and ozone application points

## Slide 52: Monthly Trends – Ozone Generator Efficiency
Inefficient generator operation trends show need for maintenance of instruments and/or generator.
Generator operation trends shows good instrument accuracy and generator efficiency since April 2014.

## Slide 53: Ozone Generator Maintenance
Monitor ozone generator efficiency trends to determine when cleaning is required
Ozone generator cleaning may be expensive and time consuming
Cleaning interval of 5 to 10 years might be expected with good operating practice
Follow other preventive maintenance activities and schedule recommended by manufacturer

## Slide 54: Ozone System Maintenance Activities

## Slide 55: Ozone Critical Control Point Monitoring (Part 1)
Depending upon the use of ozone, the control point and monitoring systems are different.
CT (residual and contact time) operation
  CT = Disinfectant (mg/L) x Contact time (minutes)
  CT targets for pathogen inactivation per EPA criteria
  Bromate formation can be problematic
  Some critical control points are downstream of ozone, using online monitoring of ozone residual and online monitoring of flow (can also be upstream) based upon known flow/contact time relationships
  Some critical control points are upstream of ozone, nitrite concentration and online monitoring of flow (can also be downstream)

## Slide 56: Ozone Critical Control Point Monitoring (Part 2)
Depending upon the use of ozone, the control point and monitoring systems are different
No residual operation
  Dose based upon a target O₃/TOC ratio (after accounting for nitrite demand)
  Target is chemical destruction, virus kill, and bacteria kill (not protozoa kill)
  Balance O₃/TOC to optimize disinfection and chemical destruction, enhance biofiltration (if applicable), and minimize bromate
  Critical control point is upstream of ozone, using online monitoring of ozone dose, nitrite concentration, total organic carbon. UVT measurements can provide a redundant method to document transferred ozone dose effectiveness

## Slide 57: Bacteria Dose/Response in Wastewater is Not Well Predicted by CT
Data Obtained from State of California Division of Drinking Water Title 22 Validation Report from H₂O Engineering and WEDECO

## Slide 58: O3/TOC Provides for Better Online Control Through Measurement of TOC Ahead of O3
Data Obtained from State of California Division of Drinking Water Title 22 Validation Report from H₂O Engineering and WEDECO

## Slide 59: Virus Disinfection too Fast for CT
59
Data Obtained from State of California Division of Drinking Water Title 22 Validation Report from H₂O Engineering and WEDECO

## Slide 60: Ozone/(TOC+Nitrite) Provides Best Virus Correlation Yet
60
Data Obtained from State of California Division of Drinking Water Title 22 Validation Report from H₂O Engineering and WEDECO

## Slide 61: Relationship Between O3Dose: TOC and Residual and CT
O3 Dose:TOC at ~0.8 develops residual and CT
Residual disappears quickly below this value
“Use of UV and Fluorescence Spectra as Surrogate Measures for Contaminant Oxidation and Disinfection in the Ozone/H2O2 Advanced Oxidation Process”, Water Reuse Research Foundation, Snyder, S.A.; Korshin, G.; Gerrity, D.; & Wert, E. (2013)

## Slide 62: Log Inactivation of Surrogate Microbes vs. CT
MS2 maximum inactivation at O3Dose:TOC ratio of 0.83
E.Coli inactivation increases as CT increases
  The challenge is: The required amount of log inactivation depends on influent concentrations
  Example 2-log (100:1, 300:3, 1000:10)
Note MS2 is a bacteriophage used as a surrogate for pathogens.

## Slide 63: Ozone Inactivation Credits Can be Obtained the “Old Fashioned Way”, Based upon CT, as is Done for ALL Conventional Drinking Water Ozone Projects
Calculate CT
Measure water temperature
Calculate Log Inactivation for CT=1 (This is called the inactivation rate, kv, kG, or kC as shown on previous slide)
Multiply “k” times measured “CT” Virus log inactivation = kv x CTmeasured Giardia log inactivation = kG x CTmeasured Crypto log inactivation = kC x CTmeasured

## Slide 64: CT Targets for Cryptosporidium
Long Term 2 Enhanced Surface Water Treatment Rule Toolbox Guidance Manual
Note: Other CT targets can be readily defined for virus and Giardia inactivation

## Slide 65: Ozone CT Monitoring Requirements
No inactivation credit for first dissolution chamber (high CT requirement for crypto)
If no tracer data to detect T, method as follows
CT credit only if there is measurable ozone residual in influent to dissolution chamber
In reaction chambers (no ozone addition) CT credit calculations depend on number of reaction chambers.

## Slide 66: How is CT Measured?
“C” is the measured oxidant residual Concentration (in this case ozone). NOTE: We define ozone in water as “residual” (e.g., 0.35 mg/L). We define ozone in the gas as “concentration” (e.g., 8.2% by weight).
“T” is actually the “T10” time, considering short-circuiting in ozone contact basins

## Slide 67: What is “HDT”, “HRT”, or “T”?
Assume the bucket holds 5 gallons of water
Or, V = volume = 5 gallons
Assume that the 1 gallon enters the bucket every minute (1 gallon/minute or 1 gpm)
How long before the bucket fills with water?
Answer = 5 minutes
HDT = “Hydraulic Detention Time” or Time “T” = V/Q = 5 gal ÷ 1 gal/min = 5 min
So, at the plant we can calculate “T” by knowing water flow and contactor cell volumes
V = 5 gal
Q = 1 gal / min

## Slide 68: Disinfection “CT” Terms
CT, in mg-min/L, is ozone residual in mg/L times “T10” time in minutes. More accurately it is CT10
Hydraulic detention time (called “T”) in minutes, is contactor ozone-exposure volume in gallons divided-by water flow in gallons per minute
T10 is the time in minutes for the CT10 calculation. Calculation for T10 time is T x T10/T ratio (90% of the water has at least this amount of contact time.)
T10/T is the contactor short-circuiting factor. More specifically, it is the time it takes before 10% of the contactor inlet water flow exits the contactor

## Slide 69: Disinfection CT and pathogen log inactivation (3 steps)
Measure CT value (actually CT10)
  “Effluent” method for CT calculation is easiest, but conservative and leads to higher disinfection by-products (DBP)
  “Integration” method for CT calculation is more accurate – less DBPs
Use LT2ESWTR Guidance Manual inactivation rate equations (Log Inactivation per CT=1)
Calculate Log Inactivation

## Slide 70: What About T10/T Ratio?
o o o
o o
o o
o o
o o o
o o
o o
o o o
o o
o o o
o o
- - - -
Tracer, e.g., 1 mg/L dose
Samples
0.0
0.1
0.2
0.3
0.4
0.5
0.6
0.7
0.8
0.9
1.0
0
3
6
9
18
Time, minutes
Tracer Concentration, mg/L
12
15
24
T10/T = 5.4 / 9 = 0.60
T = HDT = 9 min
T10 = 5.4 min
27
21
Notes: Assume “fluoride” is the tracer and the dose-pump is started when the first sample is collected (time zero). Of course, measured fluoride is zero (0). Fluoride continues to be zero for a period of time, and then suddenly fluoride shows up in the samples. Eventually, the fluoride out equals the fluoride dose, since no fluoride is lost or consumed by reaction (i.e., a good tracer). The question is, when did measured fluoride equal 10% of the dose. In this example it was 5.4 min. This is compared to the V/Q, which was 9 min in this example. The T10/T ratio is 5.4 / 9, or 0.60. Now we can calculate T10 time by knowing V/Q and T10/T ratio.

## Slide 71: Ozone Reaction Chamber – Use Multiple Chambers
< 2 chambers – CT relies on effluent ozone residual concentration from each chamber

## Slide 72: Ozone Reaction Chamber - > 3 Consecutive Reaction Chambers
3 or more chambers – extended CSTR method is used.
Monitor ozone residual concentration from at least four locations within each ozone contactor

## Slide 73: Critical Monitoring Examples for CT System

## Slide 74: Ozone Residual Measurement
Ozone bleaches indigo blue color, which is measured as absorbance @ wavelength of 600 nm
  Quantify absorbance of blank sample
  Quantify absorbance of reacted sample
Ozone residual is proportional to the difference of absorbance between blank and sample

## Slide 75: Mixing Indigo Reagent 2

## Slide 76: Gravimetric Indigo Procedure
4. Obtain final weights
2. Add 10 mL Indigo
1. Prepare Blank
3. Collect samples and analyzer readings
5. Measure absorbance of
blank and samples

## Slide 77: Residual Analyzer Verification Gravimetric Indigo
Ozone Residual Testing Spreadsheet
Spreadsheet includes details of how to conduct the Standard Methods gravimetric indigo test
Can be used with gravimetric indigo or Hach ampule grab samples
Call or email if you have questions on how to use it
Customized spreadsheet can be developed if needed

## Slide 78: Grab Sampling with Ampules
Ozone residual in sample bleaches indigo in ampule
Blank
Break tip of ampule in beaker with continuous sample flow
Grab sampling with ampules may be easier than indigo method
Disadvantages of ampule method
  More variability
  Less accurate
  More expensive
  Cannot adjust for Mn interference

## Slide 79: Ozone Pocket Colorimeter
Clean & dry the ampule.
Zero with blank (If using spectrophotometer, zero on sample and read on blank.)
Insert sample ampule, cover, and read ozone residual
May indicate lower ozone residual than indigo method
Suggested for quick check of approximate ozone residual
Use medium range ampules (0 – 0.75 mg/L)

## Slide 80: Residual Analyzer Verification Ampules
Ozone Residual Testing Spreadsheet
Verification of on line ozone residual analyzers may be conducted using gravimetric indigo or ampule grab samples

## Slide 81: Residual Analyzer Status

## Slide 82: Monitoring Transferred Ozone Dose Based Upon UVT Readings
For a specific site, once the data is generated, UVT can be used as a surrogate for transferred ozone dose and ozone effectiveness
UVT of the organic matter is transformed by ozone, raising the UVT by 10% or higher depending upon the ozone dose
Monitoring the increase in UVT verifies the delivery of ozone dose to the water
Monitoring the influent UVT in isolation documents the stability of influent water quality and provides a warning of poor feed water

## Slide 83: % UV Absorbance Reduction vs. O3Dose:TOC Ratio
UV absorbance is another method to document UVT
% Reduction in UV absorbance is proportional to O3Dose:TOC ratio
Ozone/TOC correlates to pathogen kill, and hence changes in UVT can be correlated to pathogen kill
“Use of UV and Fluorescence Spectra as Surrogate Measures for Contaminant Oxidation and Disinfection in the Ozone/H2O2 Advanced Oxidation Process”, Water Reuse Research Foundation, Snyder, S.A.; Korshin, G.; Gerrity, D.; & Wert, E. (2013)

## Slide 84: ORP Compared to O3 Residual
ORP increases quickly before ozone residual occurs
ORP rises slowly with increasing ozone residual
ORP >=800 mV is indication that residual exists, but is not a good measure of how much

## Slide 85: Example of Residual Variability
0.00
0.05
0.10
0.15
0.20
0.25
0.30
0.35
0.40
0
2
4
6
8
10
12
14
16
18
20
22
24
26
Ozone Residual, mg/L
NOTE: Ozone production and
water flow were constant
Time, min
5-sec readings of monitor
Grab sample result

## Slide 86: Critical Control Point Response Procedures
Critical Control Point Response Procedures
Critical Monitoring and Response Procedures

## Slide 87: Low CT and Low Flow Alert Procedures

## Slide 88: Ozone Low CT and Low Ozone Residual Alert Procedure

## Slide 89: Ozone Low CT and Low UVT Alert Procedures

## Slide 90: Ozone Low CT Critical Failure Response

## Slide 91: Ozone Safety

## Slide 92: Ozone Safety Objectives
What are 8-hour and 15-minute ozone exposure limits?
Is ozone gas heavier or lighter than air?
Understand difference between ozone measurement units of %wt and ppmv
What is oxygen concentration for normal and “oxygen rich” atmosphere?
How would you find an ozone or oxygen leak?
What is the significance of the “fire triangle”?

## Slide 93: Ozone Gas Characteristics
Molecular formula = O3
Invisible at normal concentrations
Has distinct pungent odor
Heavier than air (Specific Gravity =1.65)
Decomposes to oxygen molecules
  Half life at 10C ~ many days
  Half life at 40C ~ several days
  Half life at 70C ~ 2 hours

## Slide 94: Effects of Ozone Exposure

## Slide 95: Ozone Gas Concentration

## Slide 96: Health Hazards of Ozone
Acute (short term effects)
  Irritation to eyes, upper respiratory tract, and lungs
  Headache may develop but should disappear quickly after a few minutes of breathing fresh air
  Pulmonary edema (fluid build up in lungs) may occur and might be delayed for a few hours after exposure to high ambient ozone concentration (i.e. >1.5 ppmv)
Chronic (long term effects)
  Long term exposure to ozone >0.1 ppmv or short term high exposure may lead to some reduction of lung function
  Medical studies show no evidence of causing cancer, lung allergies, or harming a fetus

## Slide 97: Important Ozone Safety Concepts
Initially you can smell ozone at very low levels but may quickly acclimatize
Ambient ozone concentration may vary dramatically over short distances from a leak or off-gas source
Hand held ambient ozone monitors are very helpful to ensure your safety
Effects of ozone exposure are a function of time, ambient ozone concentration, pre-existing respiratory condition, and physical exertion
Sensitivity may vary depending on the individual and medical condition

## Slide 98: First Aid for Ozone Exposure
Move immediately to area where ambient ozone is less than 0.1 ppmv and breath fresh air
If assistance is necessary, responder should use proper PPE if ambient ozone is > 0.3 ppmv
Seek immediate medical attention (Call 911) if breathing is difficult or stopped
Perform CPR if breathing has stopped
For high exposure, keep victim lying down with head up. Do not give anything to drink
Oxygen may be administered by trained personnel
For severe eye irritation, irrigate using eye wash with tempered water and seek medical attention

## Slide 99: Typical Ozone Alarm Setpoints
Initial alarm at 0.1 ppmv - high rate ventilation starts, ozone generator operation continues
At 0.3 ppmv - generator shut down, ventilation continues
Fumes from solvents, paint, etc., or particles that absorb UV light may cause false alarm
Might need to adjust alarm levels if affected by air pollution
Background ambient ozone level may be up to 0.20 ppmv due to air pollution

## Slide 100: Leak Sources and Detection
Threaded fittings
Flanges and valve stems
Portable leak detector
Potassium iodide
Not recommended

## Slide 101: Possible Areas for Ozone Off-Gas
Residual sampling area
Contactor outlet or filter gallery
Pressure/vacuum relief valve (when enough positive pressure occurs in contactor)

## Slide 102: Ozone Off-Gassing
If ozone residual exists in the water passing out of the ozone contactors, “off-gassing” will occur and high ambient ozone may result downstream of the contactors. This may compromise safety especially in confined areas such as an enclosed filter building.
Ozone residual quenching near the end of the contactor may be required to ensure safety, especially when ozone is applied to colder, high quality water with longer half-life.
Calcium thiosulfate or sodium bisulfite are usually used for quenching ozone residual.
Hydrogen peroxide may be used for quenching if additional benefits of advanced oxidation are desired.

## Slide 103: Quenching Ozone Residual
The quenching calculator spreadsheet tools for calcium thiosulfate and sodium bisulfite to the right may be used to calculate feed rate of quenching chemical required for a given water flow rate and ozone residual. A safety factor is included because it usually takes greater than theoretical amount of quenching chemical to completely quench ozone residual. The safety factor can be adjusted based on experience. On-line ORP analyzer should be used downstream of quenching application point for optimizing quenching dose. A similar spreadsheet tool could be developed for hydrogen peroxide. Details of the calculation steps can be added.

## Slide 104: High-Voltage Safety Guidelines
Danger from current flow through body, particularly the heart
Involuntary muscle contractions may cause additional harm and possible contact with other live conductors
Don’t work alone
Do not use both hands near HV line
Wear rubber sole shoes or sneakers, or use rubber mat on floor
Do not contact possible grounds
Wear eye protection
Don’t wear jewelry or other articles that could accidentally conduct current or get caught in moving parts
Have fire extinguisher rated for electrical fires close by
Know the equipment and follow manufacturer procedures and safety guidelines when working on or around ozone generator or power supply unit

## Slide 105: Additional Ozone Safety Information
Ozone Safety Data Sheet (SDS or MSDS)
OSHA - www.osha.gov
National Institute for Occupational Safety and Health (NIOSH) www.cdc.gov/NIOSH/
Compressed Gas Association, P-34 Ozone www.cganet.com
CCOHS – www.ccohs.ca
Ozone Safe Work Practices, www.worksafeBC.com

## Slide 106: Oxygen Gas Characteristics
Ozone formed from oxygen
Molecular formula for oxygen is O2
Boiling point at 1 atmosphere is -297°F
LOX/GOX expansion ratio is ~1:850
Oxygen gives no warning, it is odorless, colorless & tasteless
Oxygen is heavier than air and may accumulate in low-lying areas

## Slide 107: Oxygen-Rich Atmosphere
Normal oxygen content in air is 21 %vol
An oxygen-rich atmosphere is >23.5 %vol
Oxygen alone is not flammable, but in oxygen-rich atmosphere risk of ignition and fire is significantly increased, and it will vigorously accelerate combustion
If ignition occurs, reaction can vary from slow combustion to violent explosion
Initiation, speed, vigor, and extent of reaction depends on concentration, temperature, pressure of reactants, and the energy and mode of ignition
Materials that will not burn in air can burn vigorously when in oxygen rich atmosphere. Resulting fire is much hotter and will propagate at much greater speed

## Slide 108: Fire Triangle
If one element is missing, fire will not occur
Typical causes of oxygen fire
  Oxygen enrichment of atmosphere
  Improper use of oxygen
  Incorrect design of oxygen systems
  Incorrect operation and maintenance of oxygen systems
  Use of materials incompatible with oxygen service
Almost anything
Almost anything

## Slide 109: Incorrect Design, Operation & Maintenance
Rapid opening or closing of valves
Too high gas velocity
Poorly located vents
Maintenance work on pressurized systems
Venting into enclosed area or confined space
Allowing system to become contaminated with particles, dust, sand, oils, greases debris, etc.
Incompatible materials
Pipe, fittings or appurtenances not cleaned for oxygen service and sealed properly

## Slide 110: Ignition Sources
Open fire or flame (cigarettes, welding, etc.)
Electrical, grinding, frictional, or static electrical sparks
Heating by compression
Friction or mechanical impact
High velocity in presence of particles

## Slide 111: Emergency Response
Shut off source of oxygen
Appropriate firefighting media include water, dry chemical (powder), or carbon dioxide
Do NOT enter or attempt rescue until ambient oxygen is less than 23.5%!
May use water spray on victim from a safe distance until safe entry can be made

## Slide 112: Workplace Considerations for Oxygen
No smoking
Keep area and equipment clean
Special lubricants may be required
Piping, gaskets, seals, valve stem packing, instruments, etc. must be suitable material and cleaned for oxygen service
Get additional maintenance oriented oxygen safety training

## Slide 113: Oxygen Safety Alarms
Audible, visual, and SCADA alarms
Initial alarm at 21.5 % vol
Timed auto-shutdown after 30-minutes at 22%vol
Immediate gas flow shut down at 23.0 - 23.5 % vol
Ambient oxygen alarms are rare at water treatment facilities using ozone
Oxygen supply will shut down when fire alarm occurs

## Slide 114: Oxygen Leak Detection
Tank or liquid piping
  Evaluate severity of leak
  Turn off oxygen if necessary
  Contact supplier for repair
Gas piping
  Spray DI water or soap solution
  Repair using proper tools and safety practices

## Slide 115: Oxygen Safety Summary
Ensure that all people expected to work with oxygen are properly trained and informed regarding risks of excess oxygen
Only use materials and equipment approved for use with oxygen. Never use replacement parts that have not been approved and cleaned for oxygen service
Wear suitable clean clothing, free from oil, grease, or other combustible contaminant
Never use oil or grease to lubricate oxygen equipment
Verify that all fire extinguishing equipment is in good condition and ready for use
Smoking is strictly forbidden in area where oxygen enrichment is possible

## Slide 116: Oxygen Safety Summary (continued)
When working in confined space where oxygen is used, isolate equipment, provide ventilation, and use oxygen analyzer. Entry only be allowed by permit issued by a trained responsible person.
If fire is occurring in oxygen enriched atmosphere do not enter or attempt rescue until ambient oxygen is below 23.5%.
If exposed to oxygen enriched atmosphere, avoid flame or any ignition source until clothing has been properly ventilated.
All oxygen apparatus and equipment must be properly identified.
Escape routes must be maintained clear at all times.

## Slide 117: Oxygen Safety Information
Oxygen safety data sheet (SDS or MSDS), OSHA, NIOSH, CCOHS, & oxygen supplier
Compressed Gas Association, www.cganet.com
  G-4, Oxygen
  G-4.1, Cleaning Equipment for Oxygen Service
  G-4.4, Oxygen Pipeline and Piping Systems
  P-39, Oxygen-Rich Atmospheres
  CGA P-45, Fire Hazards of Oxygen and Oxygen-Enriched Atmospheres
  CGA AV-1, AV-8, Videos

## Slide 118
The Water Research Foundation (WRF) is a nonprofit (501c3) organization which provides a unified source for One Water research and a strong presence in relationships with partner organizations, government and regulatory agencies, and Congress. The foundation conducts research in all areas of drinking water, wastewater, stormwater, and water reuse. The Water Research Foundation’s research portfolio is valued at over $700 million.
The Foundation plays an important role in the translation and dissemination of applied research, technology demonstration, and education, through creation of research-based educational tools and technology exchange opportunities. WRF serves as a leader and model for collaboration across the water industry and its materials are used to inform policymakers and the public on the science, economic value, and environmental benefits of using and recovering resources found in water, as well as the feasibility of implementing new technologies.
For more information, contact:
The Water Research Foundation
Alexandria, VA Office
1199 North Fairfax Street, Suite 900
Alexandria, VA 22314-1445
Tel: 571.384.2100
www.werf.org werf@werf.org
Denver, CO Office
6666 West Quincy Avenue
Denver, Colorado 80235-3098
Tel: 303.347.6100
www.waterrf.org Info@WaterRF.org
© Copyright 2018 by The Water Research Foundation. All rights reserved. Permission to copy must be obtained from The Water Research Foundation.
WRF ISBN: 978-1-60573-363-0
WRF Project Number: Reuse-15-05/4772
This report was prepared by the organization(s) named below as an account of work sponsored by The Water Research Foundation. Neither The Water Research Foundation, members of The Water Research Foundation, the organization(s) named below, nor any person acting on their behalf: (a) makes any warranty, express or implied, with respect to the use of any information, apparatus, method, or process disclosed in this report or that such use may not infringe on privately owned rights; or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of, any information, apparatus, method, or process disclosed in this report.
Hazen and Sawyer, Carollo Engineers Inc., Santa Clara Valley Water District
This document was reviewed by a panel of independent experts selected by The Water Research Foundation. Mention of trade names or commercial products or services does not constitute endorsement or recommendations for use. Similarly, omission of products or trade names indicates nothing concerning The Water Research Foundation's positions regarding product effectiveness or applicability.