## Slide 1
Adsorption Module: GAC and PAC

## Slide 2: Project Partners
Hazen and Sawyer
Carollo Engineers
Santa Clara Valley Water District
LA Sanitation District
Gwinnett County (GA)
El Paso Water Utilities
UFTREEO (University of Florida)
Sacramento State
University of Arizona-WEST Center
TrojanUV
Xylem Inc.
Process Applications Inc.
Calgon Carbon Corporation

## Slide 3: Acknowledgements to Calgon Carbon Corporation for Providing Some of the Data and Content Used in this Module

## Slide 4: Expected Learning Outcomes
Learners will be able to
  Explain the importance of adsorption for contaminant removal
  Identify direct potable reuse treatment applications for contaminant removal
  Describe adsorption theory
  Explain the risks of desorption and the impacts on water quality
  Explain adsorption isotherms
  Identify the types of adsorbents that are used
  Discuss the application differences between GAC and PAC
  Explain common operating problems and troubleshooting strategies

## Slide 5: Module Outline
Role of Adsorption in Potable Reuse
Introduction and Fundamentals
Control Philosophy
Design Criteria
Process Components
Operation and Maintenance
Safety
Available Resources

## Slide 6: Acronyms (1 of 3)
AC – Activated Carbon
ACT – Accelerated Column Test
CCP – Critical Control Point
DBP – Disinfection By-Product
DOC – Dissolved Organic Carbon
EBCT – Empty Bed Contact Time
EDC – Endocrine Disrupting Chemical
EPA – Environmental Protection Agency
GAC – Granular Activated Carbon
HAA – Halo Acetic Acid

## Slide 7: Acronyms (2 of 3)
MTBE – Methyl Tert-butyl Ether
MTZ – Mass Transfer Zone
NOM – Natural Organic Matter
PAC – Powdered Activated Carbon
PCE – Tetrachloroethylene
PFBA – Perfluorobutanoic Acid
PFC – Perfluorinated Chemical
PFOA – Perfluorooctanoic Acid
PFOS – Perfluorooctanesulfonic Acid

## Slide 8: Acronyms (3 of 3)
PPCP – Pharmaceutical and Personal Care Products
RSSCT – Rapid Small-Scale Column Tests
SCADA - Supervisory Control and Data Acquisition
TCE – Trichloroethylene
TCN – Trace Contaminant Number
TCP – 1,2,3-Trichloropropane
THM – Trihalomethane
TOC – Total Organic Carbon
UV254 – Ultraviolet Transmittance at 254 nanometers
UV/AOP – Ultraviolet Advanced Oxidation Process
VOC – Volatile Organic Compound

## Slide 9: Glossary of Terms
Word | Definition
Adsorbent | The solid media where adsorption occurs
Absorption | The process where a collectivity is taken into a volume of a permeable solid
Adsorbate | The molecules that accumulates or adsorbs onto the adsorbent material
Adsorption | The process where individual organic molecules attach onto the surface of an impermeable solid
Breakthrough | The timepoint when the effluent concentration of an organic constituent is first detected, or may be defined as when it exceeds the concentration required to be achieved by treatment.
Breakthrough Profile | The adsorbate concentration exiting the adsorbent as a function of run time
Carbon Use Rate | Mass of adsorbent used per volume of treated water
Desorption | The process in which a substance is released from a surface

## Slide 10: Glossary of Terms
Word | Definition
Empty Bed Contact Time | The amount of time water is exposed to adsorption media. Volume of bed occupied by the adsorbent divided by the flow rate
Equilibrium Isotherm | The equilibrium partitioning between the bulk aqueous-phase adsorbate-concentration and the solid-phase adsorbate-concentration at a constant temperature.
Granular Activated Carbon | Activated carbon in a granular form
Mass Transfer Zone | The region of an adsorption column in which adsorption is taking place
Powder Activated Carbon | Activated carbon in a fine powder form

## Slide 11: Role in Potable Reuse

## Slide 12: Role of Adsorption in Potable Reuse
Wastewater: Tertiary water polishing process after wastewater biological treatment
Drinking Water: Remove natural organic matter, organic chemicals, and taste and odor compounds; Used to control formation of disinfection byproducts
Typical Uses
Potable Reuse
Remove effluent organic compounds, organic chemicals, and taste and odor compounds
Provide an additional barrier against refractory organic compounds
Additional barrier to protect health (acute and chronic)

## Slide 13: Introduction and Fundamentals

## Slide 14: Adsorption is Not Absorption
Adsorption: Organic compounds attach onto the surface of an impermeable solid
Absorption: Compounds are dissolved into a volume of a permeable solid
Image
Courtesy of Calgon Carbon Corporation

## Slide 15: Activated Carbon
Activated carbon: charcoal that has been heated or otherwise treated to increase its adsorptive power
Equilibrium process
  Contaminants can desorb
Adsorption process includes four steps
Image Courtesy of Calgon Carbon Corporation

## Slide 16: Adsorption Transport Requires Four Steps
Bulk diffusion
Film diffusion
Surface diffusion
Pore diffusion
Granule
Water
Image Courtesy of Calgon Carbon Corporation

## Slide 17: Structure of Activated Carbon (10X – 100X)
Re-Agglomerated
Coal Particulates
Macroscopic Crack/Crevice
1 millimeter
10 millimeters
Voids in the Packed Bed
100X
10X
Image Courtesy of Calgon Carbon Corporation

## Slide 18: Structure of Activated Carbon (100X – 1,000X)
100 microns
Macroscopic Pores due to Re-agglomeration
Binder Residue
Re-Agglomerated
Coal Particulates
Macroscopic Crack/Crevice
1 millimeter
100X
1,000X

## Slide 19: Structure of Activated Carbon (1,000X – 1,000,000X)
100 microns
Macroscopic Pores due to Re-agglomeration
Binder Residue
Graphite plate
1000 angstroms
Localized Structure Graphitic Crystallite
1,000X
1,000,000X
Image
Courtesy of Calgon Carbon Corporation
1,000X

## Slide 20: Structure of Activated Carbon (1,000,000X – 10,000,000X)
Graphite plate
1000 angstroms
Localized Structure Graphitic Crystallite
Graphite
Platelet
Aliphatic dislocation of platelet
100 angstroms
Inter bounding
of plates
10,000,000X
1,000,000X
Image Courtesy of Calgon Carbon Corporation

## Slide 21: Structure of Activated Carbon (10,000,000X)
Fine Transport Pore
100 angstroms
Graphite platelet
of carbon structure
Adsorbate in a liquid-like state
10,000,000X
Image Courtesy of Calgon Carbon Corporation

## Slide 22: Only a Small Portion of the Activated Carbon Pores Adsorb Contaminants
AC is 99% graphite
Carbon is the base element of graphite
AC is a crude form of graphite
Imperfections result in porosity and greater surface area
Million-fold range in pore sizes in an AC granule
From visible cracks/crevices down to molecular scale pores
Only the smallest 5-fold range of pores adsorb
Some pores transport and some adsorb
GAC provides a high surface area compared to other media
Image Courtesy of Calgon Carbon Corporation

## Slide 23: Adsorption Strength Varies Between Chemicals
- C = O
- C = O
- C - O - C -
- C - OH
- C - H
- C - I
- C - Br
- C - Cl
- C - H
- C - F
- C - SH
- C – CH3
- C – NH2
- C - OH
- C - F
|
OH
Molar Volume
Saturation
  Pressure (Vapor-phase)
  Solubility (Liquid-phase)
Lower Solubility Favors Adsorption
Higher Molecular Weights Favor Adsorption
Notes: Higher MW means higher weight loading on GAC. In the picture benzene would be better adsorbed than a non-aromatic compound of similar molecular weight due to the greater amount of double bonds, but benzene would less adsorbable than napthalene (double ring structure) which is less adsorbable than anthracene (triple ring structure), etc. With saturation, the higher the solubility the less adsorbable it is. A compound (MtBE, for example) that is highly soluble in water tends to stay in the water as opposed to being adsorbed onto the carbon. That is why MtBE is not a well-adsorbed organic. (And similarly on the vapor phase side.)

## Slide 24: Carbon Based Materials Are Used to Manufacture Activated Carbon
Wood
Coconut Shells
Lignite
Bituminous Coal
Image Courtesy of Calgon Carbon Corporation

## Slide 25: The Starting Material Impacts the Performance of the Final Product
≠
Raw material dictates all of the product possibilities
Ash impurities
Density
Hardness
Transport pore structure
Adsorption kinetics
Image Courtesy of Calgon Carbon Corporation
Notes:     There are three main activated carbon product classes: coco, wood, and coal. Generally, coco is considered the best, wood is considered average, and coal is considered the lowest of the three product classes.

## Slide 26: Carbon Type Affects Contaminant Breakthrough
Chloroform Removal from Robinson Twp PA Water
0
10
20
30
40
50
60
70
80
90
100
0
50
100
150
200
250
Simulated Days
Effluent CHCl3, ug/L
Bituminous Coal #1
Coco #1
Coco #2
Bituminous Coal #2
Bituminous Coal #3
Bituminous Coal #4
Avg Inlet = 89.5
50% Breakthrough = 44.75
Data Courtesy of Calgon Carbon Corporation
Breakthrough curves allow one to compare the removal efficiencies of different carbon types
Early breakthrough with Bituminous Coal #4 suggests using a different carbon type
Bituminous Coal #2 is the preferred carbon due to the longer time for contaminant breakthrough

## Slide 27: The Mass Transfer Zone (MTZ) Moves through the Bed Until the Adsorptive Capacity of the Bed Is Exhausted Resulting in Breakthrough
Mass
Transfer
Zone
Headspace
Virgin
Saturated
Inlet
Outlet
Image Courtesy of Calgon Carbon Corporation

## Slide 28: Adsorption of Chemicals is an Equilibrium Process
Contaminants can desorb from GAC depending on equilibrium
Generally (though not always) organic matter (TOC) breaks through before other organic contaminants
Design and operation must focus on managing multiple chemical contaminants
Example:
  Although GAC is not a recommended treatment technology for nitrate, some nitrate adsorbs to GAC
  Changes in the influent nitrate concentration or water quality can result in nitrate desorption and increased effluent nitrate concentrations (nitrate peaking)
  Must provide adequate monitoring and should monitor water quality from different depths in the GAC contactor

## Slide 29: Breakthrough Curves Show Contaminant Breakthrough as Function of the Water Treated
Unpublished Data, Confidential Client
Data shown as breakthrough relative to influent concentration (Ci)
Notes: Breakthrough curves are plotted as a function of the ratio of the influent concentration over the effluent concentration as a function of the treated water volume.

## Slide 30: Shape of GAC Curves: Different Compounds Have Different Breakthrough Characteristics Both in Time and Shape
Unpublished Data, Confidential Client
Notes: Here the implications are that if you design a GAC system for PFC removal and you operate it for removal of PFOS and PFOA (blue and red lines) you will have time where compounds such as PFBA will breakthrough before PFOS and PFOA show up.

## Slide 31: Ideal Breakthrough Would Reach 100% and Remain Steady but, When Exhausted, GAC May Release Additional Contaminants, Exceeding 100%
Unpublished Data, Confidential Client
Notes: In ideal breakthrough curve, GAC adsorbs contaminants until influent concentration = effluent concentration when the GAC capacity is exhausted. In this case one would expect that the contaminants simply pass through the exhausted GAC with no change in concentration. However, that isn’t the case (see next slide).

## Slide 32: When Exhausted, GAC May Release Additional Contaminants, Exceeding 100%
Here, effluent concentration is greater than influent—leads to additional exposure
Equilibrium Process!
Unpublished Data, Confidential Client
Notes: In reality, once capacity is exhausted, GAC may strive to come back into equilibrium and will actually RELEASE contaminants resulting in a higher concentration in the effluent than the influent. This points to the need to ensure proper maintenance and replacement of GAC at defined triggers.

## Slide 33: Equilibrium Curve from Previous Slide is Demonstrated in Actual Breakthrough Data
Unpublished Data, Confidential Client
Notes: When looking back at the original data we can see that breakthrough of PFBA while it slowly returns to equilibrium concentrations at around 1000 million gallons.

## Slide 34: Typical Manufacturing Processes for Activated Carbon
Re-agglomerated
Thermal activation
Coal based products
Direct Activated
Thermal activation
Coal, coconut, and lignite based products
Chemical Activation
Chemical-thermal activation
Wood based products
Image Courtesy of Calgon Carbon Corporation

## Slide 35: Typical Activated Carbon Manufacturing Processes
Heated without oxygen
Activated with steam-air mixture
Image Courtesy of Calgon Carbon Corporation

## Slide 36: Reagglomeration Provides an Even Activation for Activated Carbon
Direct
Activation
Reagglomerated
Over activation in the outer
Part of the granule
Low Activation
Even Activation
Image Courtesy of Calgon Carbon Corporation

## Slide 37: Two Main Forms of Activated Carbon are Used in Water Treatment
http://www.drccarbon.com/Upload/PicFiles/2012.6.18_20.20.56_5226.jpg
http://www.kbytrade.com/uploadfile/201009/20/1657355985.jpg
Granular Activated Carbon (GAC)
Powdered Activated Carbon (PAC)
Typical diameters range from 1.2 to 1.6 mm
Typical diameters are less than 0.1 mm

## Slide 38: Powdered Activated Carbon For Episodic Contaminant Removal and Seasonal Taste and Odor Control (Where Applied to Surface Water)
Benefits
  Removal of contaminants
  Can be applied temporarily
  Can adjust carbon type and dose based on needs
Disadvantages
  Needs high dose and long contact time
  Increased residuals handling and disposal
  Storage concerns (fire and electrical safety hazards)
  Inhalation and Operator Safety
  Reactive operation – dosing may begin only after contaminant detected.
  Very messy material.

## Slide 39: Granular Activated Carbon for Permanent Adsorption Removal
Benefits
  Excellent removal of most contaminants
  No increased residuals or solids when compared to PAC
Disadvantages
  Permanent installation
  Carbon replacement costs can be expensive
  Costs: $9M for 10 MGD + $1.3 M/year O&M
  Need to consider breakthrough time and reactivation cycles

## Slide 40: Summary of Key GAC and PAC Parameters
Parameter | Granular Activated Carbon | Powder Activated Carbon
Application | Controls persistent organic compounds | Used to control seasonal taste and odor issues
Diameter | 1.2 to 1.6 mm | < 0.1 mm
Apparent Density | 25 to 31 lb/ft3 | 23 to 46 lb/ft3
Application Point | Post filtration or combined filtration/adsorption | Typically applied at the inlet to the advanced water treatment plant to increase contact time
Equipment | GAC contactors and yard piping | Dry feed or slurry feed systems
Operational Consideration | Provides opportunity for biological activity, which can improve contaminant removal and increase headloss across GAC beds | Typically fed as a dry powder or as a slurry Doses typically range from 1 to 100 mg/L
Advantages | Low carbon usage when compared to PAC Easy to reactivate | Easy to add to facility for seasonal control of taste and odor compounds
Disadvantages | Breakthrough when GAC is exhausted and requires capital upgrades and process modifications for GAC contactors | Cannot recover PAC and high carbon usage when compared to GAC. Can be very messy. PAC is hazardous (explosion risk). May only be dosed after water quality is impacted.

## Slide 41: Discussion Questions
How does adsorption vary from absorption?
What is activated carbon?
What is unique about the structure of activated carbon compared to traditional filter media?
How does adsorption work?
How does the compound's molecular weight affect adsorption?

## Slide 42: Design Criteria

## Slide 43: Multiple Parameters Are Used to Characterize GAC
Ash Percentage
Iodine and Molasses Numbers
Trace Contaminant Number (TCN)
Apparent Density
Bulk Density
Backwashed and Drained Density
Abrasion Number

## Slide 44: Ash Percentage Describes the Percent of Inorganic Material in the GAC or PAC
Carbon Source | Low Range (wt%) | High Range (wt%)
Bituminous Coal | 3% | 20%
Coconut Shells | 2% | 8%
Lignite | 10% | 40%
Wood | 10% | 40%
Weight % basis
A higher percent ash number means less true activated carbon structure per unit weight of media
High ash corresponds to lower adsorption capacity

## Slide 45: Iodine and Molasses Numbers Estimate the Pore Volume
Measures the loading of Iodine in mg (iodine)/g (carbon)
Indication of the surface area
Indicator of total pore volume
Test Characteristics
Micro pollutant capacity
Over 100% loading
Static test
Wetting
High molecular weight/loading applications
Iodine and molasses are used to describe the small and large pore volumes, respectively
Typical Humic Acid
Typical Tannic Acid

## Slide 46: Trace Contaminant Number (TCN) Measures the Smallest Available Pore Fraction
Measures the volume of the high energy pore structure
TCN: adsorption of acetoxime from water
TCN-G: adsorption of carbon tetrafluoride as a gas (G is for gas)

## Slide 47: Three Different Ways to Describe Density
Apparent density
  Highest density on a dry basis
  Typically ranges from 25 to 31 lb/ft3
  Simple and repeatable
  Good QC parameter
    Indicator of pore structure (low density, more porous)
    Indicator of spent carbon loading
Bulk density
  8-10% less than apparent density
  BD = 0.92 x AD
Backwashed and drained density
  15% less than apparent density
  BW&D = 0.85 x AD
Backwashed and Drained Density
(Segregated)
Apparent Density
(Fully mixed)
+/- 15%

## Slide 48: GAC Particles Break Down Over Time
Backwashing events can lead to particles colliding and abrading each other
Abrasion leads to development of fine particulate material that can plug filters and/or lead to a loss of carbon mass
Depending on application, high backwash frequency may require a harder carbon that is resistant to abrasion

## Slide 49: Abrasion Number Measures the Activated Carbon’s Resistance to Degradation
Measure particle resistance to degradation of steel balls in an agitated sieve shaker pan
% retention of mean particle diameter
Abrasion Number = (B/A)x100
Chart: Cumulative
| 2.0000000000000018 | 1.9000000000000019 | 1.800000000000002 | 1.7000000000000104 | 1.6000000000000021 | 1.5000000000000013 | 1.4000000000000012 | 1.300000000000002 | 1.2000000000000011 | 1.1000000000000021 | 1.0000000000000009 | 0.90000000000000091 | 0.80000000000000093 | 0.70000000000000095 | 0.60000000000000164 | 0.500000000000001 | 0.40000000000000102 | 0.30000000000000132 | 0.20000000000000104 | 0.15000000000000024 | 0.14000000000000001 | 0.12000000000000002 | 0
FILTRASORB 400 after test | 100 | 99.8422 | 99.4158 | 98.5525 | 96.7875 | 93.9159 | 89.4135 | 82.7311 | 73.566 | 62.2603 | 50 | 37.7397 | 26.434 | 17.2689 | 10.5865 | 6.0841 | 3.2125 | 1.4475 | 0.58416 | 0.15778 | 0
B
A

## Slide 50: Activated Carbon GAC Contactor Design
Multiple configurations available for GAC contactors
  Downflow, upflow, or pulsed beds
  Series or parallel operation
  Pressure or gravity
Empty bed contact time (EBCT) is a key design parameter, typically greater than 10 minutes
EBCT represents the amount of time water is exposed to adsorption media
Image Courtesy of Calgon Carbon Corporation

## Slide 51: Activated Carbon Filter Schematic
Track bed depth to monitor GAC loss by inserting a thin metal rod to the underdrain and measuring depth
Ensure enough space for GAC bed expansion
Monitor headloss to determine when to backwash
Image Courtesy of Calgon Carbon Corporation

## Slide 52: Biofiltration May Improve Contaminant Removal
Filtration through a granular media bed without the maintenance of a disinfectant residual across the bed
  Biological growth that provides additional contaminant removal
Biofilter beds are typically composed of sand, anthracite, GAC, or a combination of these materials.
Improves water stability and reduces DBPs
Must ensure large enough GAC media size to avoid plugging when biofilm forms
Must ensure GAC can handle abrasion from repeated backwash events
Image Courtesy of Hazen
Notes: Biofiltration can be defined as Biofiltration can be defined as filtration through a granular media bed without the maintenance of a disinfectant residual across the bed, which results in biological growth that provides additional biological treatment. Biofilter beds are typically composed of sand, anthracite, GAC, or a combination of these materials. Biofiltration has been used in Europe since the 1970, and although use in the United States has remained limited, the domestic water industry has increased its interest in biofiltration due to the ability of biofiltration to improve water stability and reduce DPBs
Biofilter beds are typically composed of sand, anthracite, GAC, or a combination of these materials.
Biofiltration has been used in Europe since the 1970, and although use in the United States has remained limited, the domestic water industry has increased its interest in biofiltration due to the ability of biofiltration to improve water stability and reduce DPBs

## Slide 53: Testing of Carbons is Critical to Developing the Right Design and the Right Operational Strategies
Why
Many factors influence the effective service life of activated carbon (temperature, pH, EBCT, concentration, competitive adsorption)
Extremely difficult to quantify without testing
Goals
Feasibility
Service Life Estimation
Types
Bench Scale (TACTIC, Isotherm, ACT/RSSCT, PAC Jar Testing)
In-Process (Pilot Column)
Product Comparison
Treatment Technology Comparison

## Slide 54: Equilibrium Isotherms Describe How Much Material Can Be Adsorbed
Isotherms describe relationship between quantity of adsorbate per units of absorbent
Determined by plotting data from batch equilibrium carbon adsorption tests
Series of carbon dosages allowed to equilibrate
INCREASING DOSE OF CARBON
Notes: Isotherms are valid for a given temperature.

## Slide 55: Equilibrium Isotherms Describe How Much Material Can Be Adsorbed
Chart: Liquid-phase Concentration (ug/L)
| 3 | 4.5 | 4.0999999999999996 | 8.1 | 15.5 | 18.899999999999999 | 24.5 | 74.3 | 57 | 109 | 162.5 | 213.6 | 144.9 | 643 | 872.6 | 1109.0999999999999 | 1476.9 | 2699.8 | 3271.9 | 4858.3999999999996 | 6263.2 | 8427.2000000000007 | 9990 | 9875.5 | 354
TCE Absorbent-Phase (ug/g) | 6061.2012 | 6998.1744 | 7975.3299 | 10267.4807 | 13888.9049 | 14888.4462 | 16523.8364 | 19439.0709 | 21982.5101 | 24640.5578 | 29011.4138 | 32494.0758 | 35405.8712 | 46540.2226 | 54259.77 | 61563.723 | 71582.997 | 80157.3258 | 92111.8552 | 94518.8502 | 108153.5177 | 112911.4798 | 123276.5833 | 119706 | 42410.6727
Chart: Liquid-phase Concentration (ug/L)
| 3 | 4.5 | 4.0999999999999996 | 8.1 | 15.5 | 18.899999999999999 | 24.5 | 74.3 | 57 | 109 | 162.5 | 213.6 | 144.9 | 643 | 872.6 | 1109.0999999999999 | 1476.9 | 2699.8 | 3271.9 | 4858.3999999999996 | 6263.2 | 8427.2000000000007 | 9990 | 9875.5 | 354
TCE Absorbent-Phase (ug/g) | 6061.2012 | 6998.1744 | 7975.3299 | 10267.4807 | 13888.9049 | 14888.4462 | 16523.8364 | 19439.0709 | 21982.5101 | 24640.5578 | 29011.4138 | 32494.0758 | 35405.8712 | 46540.2226 | 54259.77 | 61563.723 | 71582.997 | 80157.3258 | 92111.8552 | 94518.8502 | 108153.5177 | 112911.4798 | 123276.5833 | 119706 | 42410.6727
Basic Equilibrium Isotherm )
Multiple Isotherm Models/Equations are available
  Langmuir
  Freundlich
  Brunauer, Emmet, and Toller
Linear Isotherm on log-log plot
Data Courtesy of Calgon Carbon Corporation

## Slide 56: Use Accelerated Column Test (ACT) to Determine Adsorption Performance at the Bench Scale
Image Courtesy of Calgon Carbon Corporation
ACTs or rapid small-scale column tests (RSSCTs) are used to estimate GAC performance
ACTs estimate contaminant breakthrough and carbon usage requirements
Not as accurate as a full-scale GAC pilot in predicting performance and carbon usage requirements

## Slide 57: Use Pilot Columns to Evaluate and Compare GAC
Incorporates
Fluctuations in influent
Flow rate
pH
Bio-activity
Temperature
TSS
Physical filtration
Backwash
Image Courtesy of Calgon Carbon Corporation

## Slide 58: Use PAC Jar Testing to Select PAC Carbon and Determine Impacts
Example jar test below
Unfiltered raw water – with and without KMnO4
  Collected following a rain event
  Raw Water TOC = 3.8 mg/L
  Detention time of 1.1 hour
Three different PACs
Three different doses
Evaluate effect on TOC and PFCs
Image Courtesy of Calgon Carbon Corporation

## Slide 59: PAC Jar Testing – Wood-Based PAC Had Best Performance for PFCs; However GAC May Have Different Results
Chart: 6 PFC Removal with 1.1 Hour Detention Time
HDB 10 mg/L | 0.13989
HDB 25 mg/L | 0.18579
HDB 50 mg/L | 0.48087
Aquanuchar 10 mg/L | 0.19016
Aquanuchar 25 mg/L | 0.38689
Aquanuchar 50 mg/L | 0.63607
Aquasorb 10 mg/L | -0.093989
Aquasorb 25 mg/L | -0.044809
Aquasorb 50 mg/L | 0.22077
Wood-Based
Lignite
Coconut Shell
Unpublished Data, Confidential Client

## Slide 60: PAC Jar Testing—PFOS and PFOA Had Better Removal than Combined 6 PFCs; However, GAC May Have Different Results
Chart: PFOS+PFOA Removal with 1.1 Hour Detention Time
HDB 10 mg/L | 0.15358
HDB 25 mg/L | 0.20942
HDB 50 mg/L | 0.52007
Aquanuchar 10 mg/L | 0.38394
Aquanuchar 25 mg/L | 0.68935
Aquanuchar 50 mg/L | 0.90052
Aquasorb 10 mg/L | 0.0052356
Aquasorb 25 mg/L | 0.094241
Aquasorb 50 mg/L | 0.22339
Wood-Based
Lignite
Coconut Shell
Unpublished Data, Confidential Client

## Slide 61: Example PAC Jar Testing Summary for PFCs (Site-Specific)
PACs have little to no impact on PFCs at doses less than 50 mg/L
Impact of KMnO4 on PFCs is unclear—additional testing is warranted for site-specific applications

## Slide 62: Applications

## Slide 63: Typical Municipal Applications: Boxed Items are More Commonly Targeted with GAC or PAC
Typical targets for reuse include organic contaminants and additional polishing
GAC not always used in potable reuse trains
Groundwater
  TCE/PCE
  PFCs
  1,2,3-TCP
  MTBE
  EDCs/PPCPs
  Other VOCs
Surface Water
  TOC
  Algal toxins
  DBPs and their precursors
  Taste and Odor
    MIB/Geosmin
  EDCs/PPCPs

## Slide 64: Municipal Applications: TOC and DBPs
Natural Organic Matter (NOM) – Naturally occurring organic compounds formed through decomposition of aquatic life and plants
Total Organic Carbon (TOC) – Surrogate test to measure relative levels of NOM
Disinfection By-Products (DBPs) – Halogenated compounds that result from interaction between NOM/TOC and chemical disinfectants
Chloroform

## Slide 65: Adsorption is Effective for TOC Removal
Chart: Influent & Effluent TOC Levels Alabama WTP
| 42459 | 42460 | 42461 | 42462 | 42463 | 42464 | 42465 | 42466 | 42467 | 42468 | 42469 | 42470 | 42471 | 42472 | 42473 | 42474 | 42475 | 42476 | 42477 | 42478 | 42479 | 42480 | 42481 | 42482 | 42483 | 42484 | 42485 | 42486 | 42487 | 42488 | 42489 | 42490 | 42491 | 42492 | 42493 | 42494 | 42495 | 42496 | 42497 | 42498 | 42499 | 42500 | 42501 | 42502 | 42503 | 42504 | 42505 | 42506 | 42507 | 42508 | 42509 | 42510 | 42511 | 42512 | 42513 | 42514 | 42515 | 42516 | 42517 | 42518 | 42519 | 42520 | 42521
GAC Influent TOC | 1.25 | 1.28 | 1.48 | 1.34 | 1.34 | 1.41 | 1.48 | 1.37 | 1.3 | 1.5 | 1.46 | 1.5 | 1.5 | 1.24 | 1.5 | 1.48 | 1.5 | 1.46 | 1.5 | 1.44 | 2.04 | 1.34 | 1.5 | 1.77 | 1.16 | 1.18 | 1.57 | 1.5 | 1.48 | 1.24 | 1.42 | 1.43 | 1.49 | 1.5 | 1.66 | 1.55 | 1.51 | 1.66 | 1.55 | 1.32 | 1.36 | 1.51 | 1.51 | 1.46 | 1.49 | 1.6 | 1.56 | 1.9 | 1.62 | 1.75 | 1.7 | 1.62 | 2.13 | 1.43 | 1.05 | 1.55 | 1.4 | 1.41 | 1.62
GAC Effluent TOC | 0.172 | 0.235 | 0.267 | 0.201 | 0.276 | 0.261 | 0.21 | 0.179 | 0.194 | 0.568 | 0.55 | 0.583 | 0.704 | 0.573 | 0.6 | 0.586 | 0.591 | 0.746 | 0.649 | 0.64 | 0.63 | 0.583 | 0.578 | 0.574 | 0.545 | 0.568 | 0.597 | 0.642 | 0.699 | 0.688 | 0.638 | 0.737 | 0.746 | 0.691 | 0.779 | 0.721 | 0.68 | 0.718 | 0.729 | 0.676 | 0.695 | 0.631 | 0.776 | 0.701 | 0.726 | 0.853 | 0.739 | 0.716 | 0.747 | 0.761 | 0.744 | 0.729 | 0.757 | 0.755 | 0.789 | 0.868 | 0.712 | 0.762 | 0.828
Data Courtesy of Calgon Carbon Corporation

## Slide 66: Adsorption Removes Algal Toxins
By-product of cyanobacteria life cycle
  Over 3,000 known species
Two primary classes
  Hepatotoxin – affecting the liver
  Neurotoxin – affecting nerves & nervous system
Three primary toxins of interest:
  Anatoxin-A
  Cylindrospermopsin
  Microcystin-LR
Microcystin-LR

## Slide 67: Adsorption Removal of TOC and Algal Toxins
Chart: TOC and Microcystin-LR vs Simulated Days
| 0.53125 | 2.6562499999999827 | 4.7812500000000124 | 6.9062500000000124 | 9.03125 | 11.15625 | 13.28125 | 15.40625 | 17.531250000000099 | 19.656250000000099 | 21.78125 | 23.90625 | 26.031250000000099 | 28.156250000000099 | 30.28125 | 32.40625 | 34.53125 | 36.65625 | 38.78125 | 40.90625 | 43.03125 | 45.15625 | 47.28125 | 49.40625 | 51.53125 | 53.65625 | 55.78125 | 57.90625 | 60.03125 | 62.15625 | 64.281250000000227 | 66.406250000000227 | 68.531250000000227 | 70.65625 | 72.781250000000227 | 74.906250000000227 | 77.031250000000227 | 79.15625 | 81.281250000000227 | 83.406250000000227 | 85.531250000000227 | 87.65625 | 89.781250000000227 | 91.906250000000227 | 94.031250000000227 | 96.15625 | 98.281250000000227 | 100.40625000000037 | 102.53125000000037 | 104.65625 | 106.78125000000037 | 108.90625000000037 | 111.03125000000037 | 113.15625 | 115.28125000000037 | 117.40625000000037 | 119.53125000000037 | 121.65625 | 123.78125000000037 | 125.90625000000037 | 128.03125 | 130.15625 | 132.28125 | 134.40625 | 136.53125 | 138.65625 | 140.78125 | 142.90625 | 145.03125 | 147.15625 | 149.28125 | 151.40625 | 153.53125 | 155.65625 | 157.78125 | 159.90625 | 162.03125 | 164.15625 | 166.28125 | 168.40625 | 170.53125 | 172.65625 | 174.78125 | 176.90625 | 179.03125 | 181.15625 | 183.28125 | 185.40625 | 187.53125 | 189.65625 | 191.78125 | 193.90625 | 196.03125 | 198.15625 | 200.28125 | 202.40625 | 204.53125 | 206.65625 | 208.78125 | 210.90625 | 213.03125 | 215.15625
CMR F-400 TOC | 0 | 0.08 | 0.34 | 0.72 | 0.92 | 1.08 | 1.15 | 1.45 | 1.55 | 1.66 | 1.69
F-400 TOC | 0.09 | 0.14 | 0.41 | 0.72 | 0.94 | 1.01 | 1.18 | 1.35 | 1.44 | 1.49 | 1.51
Feed TOC | 2.065 | 2.12 | 2.11 | 2.17
feed toc | 2.115 | 2.115
Feed MC-LR | 55.1 | 52.3 | 58.5 | 52.7
F-400 MC-LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CMR F-400 MC-LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOC Breakthrough
No Algal Toxin Breakthrough
Data Courtesy of Calgon Carbon Corporation

## Slide 68: Adsorption for PFC Removal
PFCs are manmade fully fluorinated organic compounds
PFOS: Perfluorooctane sulfonate
PFOA: Perfluorooctanoic acid
PFBA: Perfluorobutanoic acid
PFCs are found in a number of products
Fire-fighting foams
Non-stick cookware
Water-proof/repellant outdoor gear
Food paper wrappings
Carpeting/upholstery
PFOA
PFOS
Image Courtesy of Calgon Carbon Corporation

## Slide 69: Municipal Applications: PFCs
Chart: Simulated Days of Operation vs PFCs and TOC
| 0.65145833339630277 | 2.8639583333962464 | 5.0764583333962943 | 9.5014583333962968 | 11.713958333396299 | 13.926458333396322 | 18.351458333396305 | 20.56395833339629 | 22.776458333396288 | 27.2014583333963 | 29.413958333396305 | 31.62645833339629 | 36.051458333395999 | 38.263958333396303 | 40.476458333396245 | 44.901458333395993 | 47.113958333396297 | 49.326458333396296 | 53.751458333396144 | 55.963958333396299 | 58.176458333396297 | 62.601458333396245 | 64.813958333396059 | 67.026458333394444 | 71.451458333396218 | 73.663958333395158 | 75.876458333393984 | 80.301458333395658 | 82.513958333396218 | 84.726458333395158 | 89.151458333394444 | 91.363958333395658 | 93.5764583333941 | 98.001458333396059 | 100.21395833339628 | 102.42645833339535 | 106.85145833339521 | 109.06395833339595 | 111.27645833339504 | 115.70145833339618 | 117.91395833339628 | 120.12645833339432 | 124.55145833339535 | 126.76395833339618 | 128.97645833339641 | 133.40145833339687 | 135.61395833339552 | 137.82645833339836 | 142.25145833339641 | 144.46395833339631 | 146.67645833339631 | 151.10145833339641 | 153.3139583333963 | 155.52645833339687 | 159.95145833339836 | 162.16395833339618 | 164.37645833339641 | 168.80145833339787 | 171.01395833339618 | 173.22645833339641 | 177.65145833339687 | 179.86395833339631 | 182.07645833339637 | 186.50145833339641 | 188.71395833339452 | 190.92645833339787 | 195.35145833339868 | 197.5639583333963 | 199.77645833339631 | 204.20145833339637 | 206.41395833339618 | 208.62645833339641 | 213.05145833339787 | 215.26395833339618 | 217.47645833339641 | 221.90145833339687 | 224.11395833339552 | 226.32645833339836 | 230.75145833339641 | 232.96395833339631 | 235.17645833339631 | 239.60145833339641 | 241.8139583333963 | 244.02645833339687 | 248.45145833339836 | 250.66395833339618 | 252.87645833339641 | 257.30145833339702 | 259.51395833339632 | 261.72645833339641 | 266.15145833339778 | 268.36395833339702 | 270.57645833339632 | 275.00145833339701 | 277.21395833339631 | 279.42645833339628 | 283.85145833339732 | 286.06395833339701 | 288.27645833339631 | 292.70145833339632 | 294.91395833339641 | 297.12645833339701 | 301.55145833339702 | 303.76395833339632 | 305.97645833339641 | 310.40145833339631 | 312.61395833339702 | 314.82645833339632 | 319.25145833339701 | 321.46395833339631 | 323.67645833339702 | 328.10145833339732 | 330.31395833339701 | 332.52645833339631 | 336.95145833339632 | 339.16395833339732 | 341.37645833339701 | 345.80145833339702 | 348.01395833339632 | 350.22645833339641 | 354.65145833339778 | 356.86395833339702 | 359.07645833339632 | 363.50145833339701 | 365.71395833339631 | 367.92645833339628 | 372.35145833339732 | 374.56395833339701 | 376.77645833339631 | 381.20145833339632 | 383.41395833339641 | 385.62645833339701 | 390.05145833339702 | 392.26395833339632 | 394.47645833339641 | 398.90145833339631 | 401.11395833339702 | 403.32645833339632 | 407.75145833339701 | 409.96395833339631 | 412.17645833339702 | 416.60145833339732 | 418.81395833339701 | 421.02645833339631 | 425.45145833339632 | 427.66395833339732 | 429.87645833339701 | 434.30145833339702 | 436.51395833339632 | 438.72645833339641 | 443.15145833339778 | 445.36395833339702 | 447.57645833339632 | 452.00145833339701 | 454.21395833339631 | 456.42645833339628 | 460.85145833339732 | 463.06395833339701 | 465.27645833339631 | 469.70145833339632 | 471.91395833339641 | 474.12645833339701 | 478.55145833339702 | 480.76395833339632 | 482.97645833339641 | 487.40145833339631 | 489.61395833339702 | 491.82645833339632 | 496.25145833339701 | 498.46395833339631 | 500.67645833339702 | 505.10145833339732 | 507.31395833339701 | 509.52645833339631 | 513.95145833339632 | 516.16395833339652 | 518.3764583333965 | 522.80145833339634 | 525.01395833339654 | 527.22645833339652 | 531.65145833339625 | 533.86395833339634 | 536.07645833339654 | 540.5014583333965 | 542.71395833339852 | 544.92645833339634 | 549.35145833339629 | 551.5639583333965 | 553.77645833339852 | 558.20145833339654 | 560.41395833339652 | 562.6264583333965 | 567.05145833339634 | 569.26395833339654 | 571.47645833339652 | 575.90145833339625 | 578.11395833339805 | 580.32645833339632 | 584.7514583333965 | 586.96395833339625 | 589.17645833339805 | 593.60145833339652 | 595.8139583333965 | 598.02645833339625 | 602.45145833339632 | 604.66395833339652 | 606.8764583333965 | 611.30145833339634 | 613.51395833339654 | 615.72645833339652 | 620.15145833339625
PFHpA | 0 | 0 | 0 | 0 | 0
PFHxA | 0 | 0 | 0 | 0 | 0
PFOA | 0 | 0 | 0 | 0 | 0
Feed PFOA | 0.38 | 0.31 | 0.3
TOC Removal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.195 | 0.22 | 0.28 | 0.3 | 0.34 | 0.38333 | 0.42 | 0.45333 | 0.48 | 0.46667 | 0.47667 | 0.49333 | 0.49667
Feed TOC | 0.87667 | 0.83 | 0.745 | 0.75667 | 0.7 | 0.8 | 0.89 | 0.765
Non detect after 620 simulated days of operation
Data Courtesy of Calgon Carbon Corporation
TOC Concentration

## Slide 70: GAC Provides Treatment for PFCs in Addition to Improving General Water Quality and Ensuring Compliance
Source: Calgon Carbon Corporation
195 days to TOC breakthrough
620 days to PFC breakthrough
Eff. TOC

## Slide 71: Shorter Chain PFCs Break Through Earlier and Co/Ci > 1
Unpublished Data, Confidential Client

## Slide 72: In Usage Cycles PFCs Break Through Earlier GAC Ages
Unpublished Data, Confidential Client

## Slide 73: GAC Treatment of PFCs is Complicated by Background Natural Organic Matter
WRF Project #4322
In the presence of NOM, contaminant breakthrough is sooner than in pure water
Pure Water
Natural Water With NOM

## Slide 74: Lead/Lag Series Operation Provides Additional PFC Treatment Barriers
Unpublished Data, Confidential Client

## Slide 75: Adsorption for 1,2,3-TCP Removal
TCP is a man-made, colorless, chlorinated hydrocarbon.
TCP has historically been used as a paint or varnish remover, degreaser, and cleaning agent.
TCP also has been used as a chemical in pesticides for low growing crops such as potatoes, tobacco, and beets.
1,2,3–TCP is a non-aqueous liquid with a density greater than that of water, making it difficult to remove from ground water wells.
1,2,3-TCP
Image Courtesy of Calgon Carbon Corporation

## Slide 76: Breakthrough Curves for 1,2,3-TCP
Coconut #1
Coconut #2
Bit. Coal - Virgin
Coconut #3
Bit. Coal - React
Data Courtesy of Calgon Carbon Corporation

## Slide 77: Final Takeaways
Multiple factors influence adsorption
  Base material
  Manufacturing method
  Contaminants
Testing is critical to determine feasibility and service life
Simultaneous removal of contaminants
Adsorption is an equilibrium process
  Adsorption is in competition with desorption
  Be mindful of influent water quality changes

## Slide 78: Discussion Questions
What are the typical application points for activated carbon in the WTP?
What is the MTZ?
What factors influent GAC performance?
When do contaminants desorb from GAC?
What classes of chemicals can adsorption remove?
In what situations is PAC more appropriate than GAC? And vice versa?
How can activated carbon impact disinfection performance? (in particular disinfection byproduct formation).

## Slide 79: Process Components

## Slide 80: Typical GAC/PAC Application Points
Typical PAC application point (may require additional contact time)
Typical GAC application point
(Combined filtration/adsorption)
Typical GAC application point
(GAC Contactors)
Image Courtesy of Calgon Carbon Corporation

## Slide 81: Typical GAC Contactor Configuration
Image Courtesy of Calgon Carbon Corporation

## Slide 82: Common GAC/PAC Equipment
Item | Purpose
Bag Loading Hopper | Fill bags with dry materials
Dust Collector | Collects and removes dust
Eductor | A jet pump that uses the Venturi effect to create the PAC slurry
Flow Meters | Monitor chemical feed and water flow
GAC Contactor | Concrete or steel tank that houses the GAC and provides an adequate contact time.
GAC Support System (Sand or Gravel) | Supports GAC bed
Hopper | Stores and distributes dry material
Laboratory Equipment | Measure water quality parameters
Mixers | Ensures dispersion and complete mixing of chemicals

## Slide 83: Common GAC/PAC Equipment
Item | Purpose
Positive Displacement Pumps | Feed liquid chemicals (disinfectants)
Pressure Gauges | Used to monitor headloss across the bed
Pumps and Backwash Pumps | Used to push water though system and backwash contactors
Sampling Ports | Used to sample the contaminant as they move through the GAC bed
Storage Bins | Dry chemical storage
Tanks | Store chemicals and or PAC slurry
Trucks | To change out media
Underdrain laterals and connector | Routes GAC effluent to next process
Valves | Start, stop, adjust flows, and switch between lead/lag vessels

## Slide 84: Control Philosophy

## Slide 85: Activated Carbon Usage Strategies
GAC must be reactivated or replaced when breakthrough exceeds a given trigger (e.g., when TOC > 1 mg/L)
GAC may also be used to keep UVT (ultra violet light transmittance) high for downstream UV (Ultra violet) or UV/AOP (UV Advanced Oxidation processes) (e.g., UVT > 95%)
Failure to reactivate or replace GAC at trigger values can cause excess TOC breakthrough resulting in TOC spikes

## Slide 86: Activated Carbon Control Strategies
Monitor effluent turbidity, TOC, UVT254, and EBCT (flow rate) to monitor age of GAC and breakthrough of contaminants
Control strategies include
  Decrease flow to increase EBCT if EBCT is too low
  Replace\reactivate GAC
  Increase amount of activated carbon

## Slide 87: Critical Control Point (CCP) Response Procedures Define What to Do When Control Limits Exceed Alert Value

## Slide 88: Critical Control Point (CCP) Response Procedures Define What to Do When Control Limits Exceed Alarm Value/ Critical Limit

## Slide 89: Control Recommendations
Good operations
  Maintain High EBCTs > 10 minutes
  Replace GAC before effluent TOC concentration and UVT triggers
  Periodic review of carbon replacement history
STABILITY is key
  Review SCADA trends
  Proactive GAC replacement/reactivation

## Slide 90: Operation and Maintenance

## Slide 91: The Challenge for DPR Operations Teams
Upstream changes in water quality could change adsorption equilibrium
Competitive adsorption and adsorption equilibrium processes can release contaminants that were adsorbed from GAC

## Slide 92: Optimizing the GAC Configuration Will Improve Treatment
Evaluate Lead/Lag operation
>10 min EBCTs
Image Courtesy of Calgon Carbon Corporation

## Slide 93: Process Monitoring for Adsorption
Monitor GAC effluent turbidity, TOC, and UVT254
Monitor EBCT
Measure rate of carbon loss
  Use distance between top of the bed and a fixed point
  Perform GAC bed cores to evaluate life
Use laboratory staff to test for contaminants and to verify the adsorptive capacity of the media
  Check contaminant removal
  Perform biological tests to verify if GAC is biologically active

## Slide 94: Other Implications of GAC Need to be Considered
Optimize the EBCT, hydraulic loading rate, and bed depth to maximize the GAC bed life
  Higher EBCTs improve GAC life
GAC may change water pH
GAC quenches any oxidants present (e.g., chlorine, KMnO4)
Explosion hazard (dust)
Storage safety (to be discussed)

## Slide 95: Other Implications of PAC Need to be Considered
PAC may change water pH
PAC quenches any oxidants present (e.g., chlorine, KMnO4)
PAC increases residuals handling & disposal
PAC needs sufficient contact time
PAC needs sufficient velocity to avoid settling
Storage challenges—messy, PAC requires special feed equipment
Possible explosion and/or fire hazard (dust)
Storage safety (to be discussed)

## Slide 96: Support from Laboratory Personnel is Essential for Evaluating Adsorption Process
Ensure analyzers are maintained and calibrated (TOC and UVT)
Use standards (positive controls) and blanks (negative controls)
Evaluate the precision and accuracy of instruments
<http://kaffee.50webs.com/Science/images/Accuracy-vs-precision1.jpg>

## Slide 97: Don’t Blindly Trust Data, Statistics, or Models
Perform positive and negative controls in the laboratory to verify analysis
Statistics and models can mislead
  Carefully evaluate data
Test adsorption processes to evaluate and confirm functionality
Use spreadsheets to chart data trends and investigate changes in data
QA/QC


## Slide 98
Preventative Maintenance and Troubleshooting for PAC
Routinely check tanks, feed lines, and pumps for leaks and/or damages
Use a good design practice to minimize dust associated with PAC
Ensure all PAC slurries are continuously mixed to prevent clogging

## Slide 99
Preventative Maintenance and Troubleshooting for GAC
Inspect GAC contact tank and underdrain system during GAC changeout
Measure carbon losses in the GAC bed
Typical carbon loss is between 1% to 4% a year
High carbon loss suggests excessive backwash rate or underdrain problems

## Slide 100: Discussion Questions
When should GAC be used over PAC and vice versa?
What causes carbon loss in the filter?
How can handling issues associated with dry PAC be mitigated?
What is the shape of a typical breakthrough curve?
What information does an equilibrium isotherm provide?

## Slide 101: Safety

## Slide 102: Multiple Safety Hazards Exist with Activated Carbon
Activated carbon is flammable
  Proper storage is essential
  Minimize dust
Activated carbon conducts electricity
  Motor heat can ignite dust, leading to short-circuiting and fires
  Minimize dust with bag type dust collectors or other means
Wet activated carbon removes oxygen (O2)
  Suffocation danger in enclosed spaces (slurry tanks)
Notes: GAC and PAC depletes oxygen, especially if wet – do not enter confined spaces until air tests show safe – even large contactor – ventilate strongly
Dust from GAC and especially PAC is deleterious to respiration and can lead to chronic breathing problems – use respirator and goggles or full face respirator
Dust explosions, deflagrations, detonations and fires cause fatalities and injuries
All electrical equipment in PAC dry handling areas must be Class II Division 2 minimum – do not forget fire detection, instrumentation and security devices
Segregate electrical equipment from dusty areas wherever possible

## Slide 103: Use Appropriate Gear to Prevent Dust Inhalation
Closed toed shoes, protective clothing, gloves, and eye protection are required at a minimum when handling activated carbon
Provide masks, shields, aprons, and shower facilities
PAC weakly explosive—requires active dust management

## Slide 104: Activated Carbon Storage Considerations
Ensure that storage areas are fireproof
Activated carbon burns like charcoal (minimal flame and smoke)
Self closing doors
Do not store near chlorine and permanganate
Do not use high pressure sprays to put out activated carbon fires
http://insidetailgating.com/wp-content/uploads/2015/05/charcoal.jpg
Notes:     Spray will disperse activated carbon
    Use fire extinguishers or fine mist sprayers

## Slide 105: National Electrical Code NEC / OSHA
http://www.osha.gov/doc/outreachtraining/htmlfiles/hazloc.html
Prevent dust buildup by good house keeping – use special vacuum cleaners to remove settled dust – do not use a brush!

## Slide 106: Class II Division 2 – PAC and GAC Requirements
http://www.osha.gov/pls/oshaweb/owadisp.show_document?p_table=STANDARDS&p_id=10750
Powdered Activated Carbon (PAC) facilities exposed to dry powder conditions shall have electrical equipment rated to Class II Division 2 at a minimum.
Granular Activated Carbon (GAC) is submerged when in use, dust is not present, and therefore does not require special electrical facilities. It is in slurry form when being removed and replaced and therefore dust should not be present.

## Slide 107: Misc. Slides without a home.

## Slide 108: Required Training Materials
Whiteboard
Colored markers
Note cards
Paper with pens and pencils
Calculators and/or computer

## Slide 109: EBCT Worksheet
Goal: To determine how the flow rate impacts the EBCT
Materials: Computer, facility data, GAC bed size, typical flow rates
Method:
  Obtain typical flow rates to GAC beds and/or contactors and GAC bed volume.
  Plot the EBCT as a function of the min and max flow rates through the GAC beds and/or contactors.
  Discuss impacts of EBCT on GAC breakthrough and strategies to optimize the EBCT.

## Slide 110: Timeline (1 of 2)
Goal: To understand typical GAC replacement frequency and degradation
Material: Computer with spreadsheet program, data concerning GAC replacement and coring/sampling
Method:
  Have operators obtain data relating to GAC from their facilities.
  Arrange GAC replacement events in a vertical column with oldest events at the top.
  Add comments next to each event on the timeline

## Slide 111: Timeline (2 of 2)
Method:
  Discuss trends that emerge within the group
  Discuss long-term implications for trends and develop schedules to maintain and replace GAC.
  Form a larger group from the sub-groups. Have each group discuss the observed trends.

## Slide 112: Live Scenario (1 of 2)
Goal: To provide the operators practice of what to do in case of a process failure/upset
Material: Whiteboard, colored markers, index cards
Method:
  Brainstorm a set of scenarios with the operators in which a component of adsorption fails. Examples include PAC feed pump failure, sudden water quality changes, contaminant breakthrough, media replacement, etc.
  Write down each scenario on an index card.
  Break the operators into small groups, and have each group pick a scenario. Ensure a good mix of senior and junior operators in each group.

## Slide 113: Live Scenario (2 of 2)
Method:
  Give each group 10 to 15 minutes to brainstorm a set of steps that can be used to correct the problem.
  Allow each group 5 to 10 minutes to present on the proposed strategy to mitigate the problem.

## Slide 114
The Water Research Foundation (WRF) is a nonprofit (501c3) organization which provides a unified source for One Water research and a strong presence in relationships with partner organizations, government and regulatory agencies, and Congress. The foundation conducts research in all areas of drinking water, wastewater, stormwater, and water reuse. The Water Research Foundation’s research portfolio is valued at over $700 million.
The Foundation plays an important role in the translation and dissemination of applied research, technology demonstration, and education, through creation of research-based educational tools and technology exchange opportunities. WRF serves as a leader and model for collaboration across the water industry and its materials are used to inform policymakers and the public on the science, economic value, and environmental benefits of using and recovering resources found in water, as well as the feasibility of implementing new technologies.
For more information, contact:
The Water Research Foundation
Alexandria, VA Office
1199 North Fairfax Street, Suite 900
Alexandria, VA 22314-1445
Tel: 571.384.2100
www.werf.org werf@werf.org
Denver, CO Office
6666 West Quincy Avenue
Denver, Colorado 80235-3098
Tel: 303.347.6100
www.waterrf.org Info@WaterRF.org
© Copyright 2018 by The Water Research Foundation. All rights reserved. Permission to copy must be obtained from The Water Research Foundation.
WRF ISBN: 978-1-60573-363-0
WRF Project Number: Reuse-15-05/4772
This report was prepared by the organization(s) named below as an account of work sponsored by The Water Research Foundation. Neither The Water Research Foundation, members of The Water Research Foundation, the organization(s) named below, nor any person acting on their behalf: (a) makes any warranty, express or implied, with respect to the use of any information, apparatus, method, or process disclosed in this report or that such use may not infringe on privately owned rights; or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of, any information, apparatus, method, or process disclosed in this report.
Hazen and Sawyer, Carollo Engineers Inc., Santa Clara Valley Water District
This document was reviewed by a panel of independent experts selected by The Water Research Foundation. Mention of trade names or commercial products or services does not constitute endorsement or recommendations for use. Similarly, omission of products or trade names indicates nothing concerning The Water Research Foundation's positions regarding product effectiveness or applicability.