## Slide 1: Biofiltration (Intended as Supplement to GAC and Ozone Modules)

## Slide 2: Project Partners
Hazen and Sawyer
Carollo Engineers
Santa Clara Valley Water District
LA Sanitation District
Gwinnett County (GA)
El Paso Water Utilities
UFTREEO (University of Florida)
Sacramento State
University of Arizona-WEST Center
TrojanUV
Xylem Inc.
Process Applications Inc.
Calgon Carbon Corporation

## Slide 3: Acknowledgements to Xylem for Providing Some of the Data and Content Used in this Module

## Slide 4: Expected Learning Outcomes
Learners will be able to…
Identify the benefit of using biologically activated filters (BAFs) for potable reuse applications
Identify critical monitoring surrogates for process control
Explain parameters influencing biological filtration
Expand knowledge acquired from O₃ and GAC modules

## Slide 5: Acronyms
AOC – Assimilable Organic Carbon
ATP – Adenosine Triphosphate
BAF – Biologically Active Filter
BDOC – Biodegradable Dissolved Organic Matter
CECs – Contaminants of Emerging Concern
COD – Chemical Oxygen Demand
D – Diameter
DBPs – Disinfection By-Products
DO – Dissolved Oxygen
DOC – Dissolved Organic Carbon
EBCT – Empty Bed Contact Time
EDCs –Endocrine Disrupting Chemicals
EPA – Environmental Protection Agency
EPS – Extracellular Polymeric Substances
GAC – Granular Activated Carbon
GW – Groundwater
H – Height
HPC – Heterotrophic Plate Count
L – Length
L – Liter
mg – Milligram
mgd – Million Gallons per Day
MIB – 2-Methyl-Isoborneol
NDMA – N-Nitrosodimethylamine
NTU – Nephelometric Turbidity Unit
PCR – Polymerase Chain Reaction
PLFA –Phospholipid Fatty-acid Analysis
RO – Reverse Osmosis
SW – Surface Water
T&O – Taste and Odor
TDS – Total Dissolved Solids
TKN –Total Kjeldahl Nitrogen
TOC – Total Organic Carbon
TOrC – Trace Organic Compound
TRFLP – Terminal Restriction Fragment Length Polymorphism
TSS – Total Suspended Solids
UF – Ultrafiltration
UV – Ultraviolet
UVT – Ultraviolet Transmittance
WE&RF – Water Environment & Reuse Foundation
W – Width
WTP – Water Treatment Plant

## Slide 6: Module Outline
The role of BAF in potable reuse
What BAF is and how it works
Process specific considerations
Operation, monitoring, and maintenance priorities for a BAF system
Critical monitoring and response procedures
Safety considerations specific to BAF

## Slide 7: Role in Potable Reuse

## Slide 8: Potable Water Reuse Requires Multiple Barriers for Reliable Purification
Target | WWTP | UF | RO | UV/AOP
Protozoa | X | X | X | X
Virus | X |  | X | X
MCLs | X |  | X | X
CECs | X |  | X | X
Target | WWTP | Ozone | BAF | UF | GAC | UV/AOP
Protozoa | X | X | X | X |  | X
Virus | X | X |  | X |  | X
MCLs | X | X | X |  | X | X
CECs | X | X | X |  | X | X

## Slide 9: Biofiltration, Coupled with Ozone, Provides a Core Treatment Barrier for Non-RO Systems
Target | WWTP | Ozone | BAF | UF | GAC | UV/AOP
Protozoa | X | X | X | X |  | X
Virus | X | X |  | X |  | X
MCLs | X | X | X |  | X | X
CECs | X | X | X |  | X | X

## Slide 10: For Some Projects, O₃/BAF is Coupled with RO-based Treatment
Ozone
Biologically
Active
Filtration
Ultrafiltration
Reverse Osmosis
Ultraviolet Disinfection Advanced Oxidation
Photo: San Diego California Permanent Potable Reuse Demonstration System
Secondary or Tertiary Effluent

## Slide 11
Ozone
Biologically
Active
Filtration
Ultrafiltration
Granular Activated Carbon
Ultraviolet Disinfection
Photos: Altamonte Springs FL Permanent Direct Potable Reuse Demonstration System
Secondary or Tertiary Effluent
Virus kill
Protozoa removal
TOC reduction
Trace chemical pollutant reduction
The Ozone/BAF Process is Critical to Non-RO Purification

## Slide 12: BAF is the Ideal Treatment to be Coupled with Ozonation
Ozone fractures recalcitrant organics, increasing biodegradation potential through BAF
Ozone hyper-oxygenates the water flowing into the BAF, again improving performance
http://www.werf.org/c/KnowledgeAreas/WaterReuse/ProductsToolsnonWERF/2017/How_Reuse_Works_Videos.aspx

## Slide 13: BAF is the Ideal Treatment to be Coupled with Ozonation
Removal/reduction of organic carbon, CECs, pathogens (filtration), and DBP minimization
  20 - 40% removal of TOC
  Destroys recalcitrant organic carbon
  O₃/BAF removes ~90% of CECs below MRL
Reduces oxidation by-products (e.g. NDMA)
Filtration of turbidity and suspended solids
  Increases UVT, making subsequent UV processes more efficient
  Source: pureALTA Direct Potable Reuse Demonstration, Altamonte Springs, FL

## Slide 14: Total Organic Carbon Removal, Step by Step through Non-RO Purification
  Source: pureALTA Direct Potable Reuse Demonstration, Altamonte Springs, FL

## Slide 15
NDMA Formed from Ozonation is Successfully Removed in Biofiltration
MDL= 2.9 ng/L
  Source: pureALTA Direct Potable Reuse Demonstration, Altamonte Springs, FL

## Slide 16: CECs, PPCPs, PFCs are Removed Through O₃/BAF
Antibiotic: Treats/prevents infections
Data shows results from 6 sampling events in 2017
  Source: pureALTA Direct Potable Reuse Demonstration, Altamonte Springs, FL

## Slide 17: CECs, PPCPs, PFCs are Removed Through O₃/BAF
Treats depression, OCD, bulimia nervosa, and panic disorder
Data shows results from 6 sampling events in 2017
  Source: pureALTA Direct Potable Reuse Demonstration, Altamonte Springs, FL

## Slide 18: BAF Fundamentals

## Slide 19: Biological Active Filtration Combines Filtration with Natural Microbial Metabolism to Reduce Contaminants and Pathogens
BAF is Biofiltration
  Can utilize activated carbon, sand, or other media substrates
  Acts as a media filter, but with increased filtration ability due to biofilms and reduced effective pore size
  Biological growth reduces a broad range of pollutants through biodegradation
  When new, a granular activated carbon (GAC) biofilter can also remove pollutants through adsorption.
In Wastewater with Ozone Pretreatment…
  Supplemental carbon and nutrients unnecessary in most cases
  Aerobic conditions are maintained
  Quenching of ozone unnecessary

## Slide 20: Biological Active Filtration Combines Filtration with Natural Microbial Metabolism to Reduce Contaminants and Pathogens
BAF Examples
  River bank filtration
  Soil Aquifer Treatment (SAT)
  Slow sand filtration
  Rapid rate filtration with/without chlorine (sand, anthracite, GAC)
  In isolation (without ozone pretreatment), BAF only treats readily biodegradable substances

## Slide 21: Biological Treatment Leverages Natural Microbial Metabolism to Reduce Contaminants and Pathogens
BAF Treatment Provides
  Reduction in Disinfection Byproduct precursors
  Pathogen removal based upon turbidity reduction and EPA criteria
  Reduction of organic and inorganic chemical constituents
  Reduces biological regrowth in water distribution systems

## Slide 22: One type of biofiltration is conventional granular media carbon (GAC) filtration, allowed to be biological
Granular Media Filtration
Chlorine
Biofiltration
-
=

## Slide 23: Biofiltration is Often Conventional Granular Media Carbon (GAC) Filtration, Allowed to be Biological
Microbial
aggregates
Biofilm
Granular media
Active Processes
Growth
Decay
Attachment
Detachment
Biodegradation
Filtration
Particles
Biological Activity Reduces Effective Pore Size, Improving Performance

## Slide 24: Filter Productivity Can Decrease After Conversion to Biofiltration
Chart: Year of Operation
| 2001 | 2002 | 2003 | 2004 | 2005
Ave UFRV | 11600 | 7300 | 6600 | 6200 | 5800
Biofiltration Implemented
Notes: Figure 1.2

## Slide 25: Other Types of Media Can be Used for BAF, Though Biodegradation Performance Efficiency is Reduced
Anthracite
Tripack
Biofill
Biochar
Spent (and regenerated) GAC
Fresh GAC
  Sources: WRF Project Reuse-13-10: Controlling Trace Organic Compounds Using Alternative Non-FAT Technology for Potable Water Reuse
  WRF Project Reuse-14-16: Pathogen Risk Evaluation of Treatment and Monitoring System Performance for Potable Reuse
Best Performance

## Slide 26: Biofilters Work Hard…for “Free”
Reduce T&O
Reduce DBPs
Reduce ammonia, iron, manganese
Reduce regrowth potential
Reduced corrosion potential
Improved disinfectant stability

## Slide 27: Ozone Upstream of Biofiltration Increases Concentration of Microbial Food
Ozone
Non-Degradable Organics
BDOC

## Slide 28: Bacteria Oxidize and Reduce Contaminants to Generate Energy and Grow
electron acceptors
macro nutrients
electron donors
For O₃/BAF in wastewater, addition of supplemental carbon or nutrients often not needed
Notes: This slide is intended to identify biotreatment as broadly as possible. It covers aerobic (oxygen as the terminal electron acceptor), anoxic (nitrate as the terminal electron acceptor), and anaerobic (perchlorate, hexavalent chromium, etc. as the terminal electron acceptor) applications. It also shows (1) the various electron donors that may be involved like organic carbon (TOC, dosed acetic acid), ammonia, manganese, and iron, (2) end-products that may be expected, (3) generation of cells, and (4) generation of extracellular polymeric substances (EPS), which is the sticky component holding biofilms together.
Ammonia-nitrogen is a critical macro-nutrient (gets assimilated into cells), but ammonia can be also be an electron donor (e.g., biological nitrification application). The “NH3” shown together with “P” is there to emphasize that in addition to electron donors and electron acceptors, bacteria need macro-nutrients like phosphorus and nitrogen to grow cells. Many waters can be P or N limited, so it’s possible that a biofiltration application will include a nutrient dosing component.

## Slide 29: Effective Biofiltration Requires a Nutritional Balance
Notes: This slide only focuses on aerobic biofiltration but also includes a nod to the fact that trace organic compounds can be removed through secondary metabolic activity during aerobic biofiltration. The “Effective biofiltration requires a nutrient balance” title is used because there is typically a follow on slide (see below) that shows when the nutrients are missing, fewer cells are generated, while more EPS is produced, which can caused hydraulic problems within a biofilter.

## Slide 30: Nutrient Limitations Create Stressed Biofilter Conditions
Biodegradable Organic Carbon
Oxygen
EPS
Intermediates, Carbon Dioxide, Water
Notes: Slide contains animation to help present concept
Enzyme

## Slide 31: Important Ozone Notes

## Slide 32: Ozone Addition Ahead of BAF Must Consider Several Impacts
Ozone
Sufficient dose to optimize TOC removal through BAF
Minimized dose to limit bromate and other ozonated DBP formation
Sufficient dose to meet disinfection targets
  Bacteria
  Virus
  Protozoa

## Slide 33
Source: Altamonte Springs FL Permanent Direct Potable Reuse Demonstration System
O₃:TOC Dosing Scheme. Ran at 0.8 to 1.3 mass ratio
Provided for 5+ log reduction of virus and 4+ log reduction of bacteria
No protozoa credits sought
TOC reduction optimized at 1.3 mass ratio, ~35% reduction
No Bromate Formed
NDMA formed by ozone, but removed by BAF
Ozone Dosing Approach and Results Example

## Slide 34: Control Philosophy

## Slide 35: O₃/BAF Control Concept (Ozone Focus)
Key parameters that impact ozone effectiveness are TOC and NO2-N, the higher these concentrations, the less effective ozone can be.
UVT254 (UV at 254 nanometers) can be used as a site-specific metric of ozone oxidation performance, where a specific dose will result in a reliable increase in UVT at 254 nanometers. UV254 is thus a performance check on ozone dose.
An O₃/TOC ratio, in the range of ~0.7 to ~1.3, can provide robust bacteria and virus kill and result in relatively low ozonated DBP formation (bromate and NDMA).
Coupled with BAF, the O₃/TOC ratio can be coupled with empty bed contact time to optimize TOC and CEC reduction
TOC
UVT254
NO2
UVT
UVT

## Slide 36: O₃/BAF Control Concept (BAF Focus)
Adding online measurements of flow, TOC, UV254, DO, and turbidity, across the O₃/BAF system provides the following:
  Turbidity reduction by filtration, correlating to pathogen removal
  TOC reduction across BAF, a direct measurement of BAF functionality
  UVT increase across BAF, a secondary measure of BAF functionality
  DO values and reduction across BAF, documenting aerobic conditions and BAF functionality
TOC
UVT254
UVT
NO2
Turbidity
DO
TOC
Turbidity
UVT
UVT
DO

## Slide 37: Long List of Online and Offline Monitoring Methods for Process Control and Optimization
Biological
DO
ATP
Enzyme Activity
HPC
EPS
PLFA
Microbial community analysis (TRFLP/PCR)
Organic Carbon
TOC
DOC
BDOC
AOC
Carboxylic Acids
UV254
UV/VIS Spectra
SUVA
Fluorescence Spectroscopy
Water Quality
Temperature
pH
Turbidity
Nutrients (N & P)
DBP Formation Potential
Calculated ozone dose!

## Slide 38: Monitoring Surrogates at Critical Control Points
Monitoring at CCPs | Value | Method
TOC | Impacts effective ozone dose, documents effective BAF operation and minimization of DBP precursors | Online
UV254 | Correlates to effective ozone dose | Online
Ozone Dose | Direct ratio to pathogen disinfection | Calculation
Nitrite | Impacts effective ozone dose | Online
Turbidity | Indirect measurement for pathogen removal through filtration | Online

## Slide 39: EBCT and Filtration Flux Impact Performance
Empty Bed Contract Time (EBCT)
  Measurement of time within the BAF filter bed (when empty)
  Values can range depending upon the target pollutants and effluent quality.
  Example EBCTs can be from 5 to 15 minutes
Filtration Flux
  Calculated as gallons per minute per square foot of filter media
  Typical values are in the 3 to 7 gpm/ft2 range
Additional Information can be found in the GAC module

## Slide 40: Dissolved Oxygen (DO) Can Be Used as a Tool to Assess Biological Activity
DO is the amount of gaseous oxygen dissolved in the water.
Concentration of DO in water is affected by temperature.
DO Important for online monitoring of biological activity in system. If an upset in the BAF occurs, the dissolved oxygen concentration in the BAF effluent should also change
Hach – www.hach.com
One Example of the Reduction of DO across biofiltration (courtesy of IDE Technologies)

## Slide 41: Adenosine triphosphate (ATP ) Measurement Provides a Direct Indication of the Microbiological Content in the Sample
Important for developing the baseline performance of the BAF and for period verification of biological activity
ATP is present in all living cells regardless of whether they are bacteria, fungi, or any other type of microbe
This method uses the luciferase enzyme isolated from firefly
Consumes ATP and Luciferin to produce light
LuminUltra®
Cathy Keifer – Livescience.com
Notes: https://www.luminultra.com/wordpress/media/LTL_Flyer_Drinking-Water_2016.pdf
http://www.livescience.com/32677-what-makes-fireflies-light-up.html

## Slide 42: Design Criteria

## Slide 43: Conventional Biological Filter Design and Management
Conventional Filters
L/D ratio
Media type
Media effective size
Media uniformity coefficient
Filter loading rate
Backwash rate & duration
Backwash auxiliary scour type
Biological Filters
Empty bed contact time
Compounds targeted for removal
  TOC
  CECs
  DBP formation potential
  Turbidity
Media Type
Pre-oxidation (Ozone)
Nutrients

## Slide 44: Operation and Maintenance

## Slide 45: The Best Biofiltration Optimization Strategies Often Require Minimal Investment
Upstream Ozone process optimization
  Balance disinfection with DBP formation
  Sufficient Ozone dose to optimize TOC reduction
Backwash rates
  Sufficient to minimize headloss
  Minimized to maintain robust biological growth
  Backwash waste sent to wastewater treatment plant headworks for recirculation and treatment
Media selection
  Regenerated GAC is best
  Other options possible
Loading rate and EBCT
  Water quality target specific
Underdrain Design and Pressure monitoring
Biofilm enhancement and fouling control
  Potential nutrient addition
Rohan van Eden, 2015
Notes: The Design of a Biophilic Wastewater Treatment Facility in Diepsloot
Rohan van Eden, 2015 https://issuu.com/rohanvaneeden/docs/rohan_thesis_binder

## Slide 46: Level of Control Over Parameters Influencing Biological Filtration
 | Degree of Control () or Effect () |  |  | 
Parameter | None | Low | Moderate | High
Media Type |  |  |  | 
Filtration rate (EBCT) |  |  |  | 
Ozone dose |  |  |  | 
Backwashing method |  |  |  | 
BOM loading |  |  |  | 
Temperature |  |  |  | 
Time for Acclimation |  |  |  | 
Source: Huck et al. 2000 (AwwaRF Report 90793), with addition of ozone dose for O3/BAF operation

## Slide 47: Backwashing Strategy May be the Most Important Operational Component of Any BAF Process
Maintains uniform hydraulic flow
Removes particles, excess biomass  controls head loss
May diminish performance at lower temperatures
Backwashing too often can result in filter instability

## Slide 48: Backwash Intervals Between 24 - 36 hours
 | Day 0-4 | Day 4-10
Sequence | Backwash only every 24h | BW + Bump every 36h
BW sequence: Air scour + High rate water + Low rate water
Bump is a gentle water only BW to breakdown the cake layer that retained on filter top

## Slide 49: Troubleshooting

## Slide 50: Biofiltration Troubleshooting Based Upon Potable Water Experience
WRF Project #4496
Issue | Indicators | Potential Causes
Hydraulic Performance | Flow Rate, headloss, unit filter run volume, filter run time, filter effluent turbidity, particle counts | Malfunctioning valves, faulty monitoring instruments, backwash pumping rates, faulty upstream processes pass more particles, changed influent water quality (temperature, solids, nutrients, pH, etc.), excess biomass, change of backwash chemical effectiveness,
Contaminant or Turbidity Breakthrough | Elevated effluent counts of particles, turbidity, TOC, DOC, UV254, carboxylic acids, aldehydes, various contaminants | Poor biological growth and activity, faulty feed pumps that impact hydraulic loading rates, inadequate backwash, changed influent water quality (see above),
Poor Biological Growth and Activity | Changes in ATP, carboxylic acids, aldehydes, TOC, AOC, BDOC | Low influent biodegradable organic matter, low influent nutrients, changed temperature, changed pH,

## Slide 51: Case Study of O₃/BAF for Water Reuse

## Slide 52: Xylem Oxelia O₃/BAF Pilot Study
The pilot study was conducted at Western Butler County Authority WWTP in Zelienople, PA - a tertiary, aerobic biological treatment facility with a hydraulic capacity of 2.2 MGD
Aeration Tank
Clarifier
Bar Screen
Sand Filtration
Chlorination
Discharge
Sludge Process & Disposal
Returned Sludge
O₃/BAF pilot

## Slide 53: O₃-BAF Pilot System
Ozone System
Contact Tank
Bio-filter
Flowrate | 5 – 25 GPM
Ozone Generation System | PSA O2 on-site concentrator + WEDECO GSO system
Ozone Dose | 0 - 25 ppm
Ozone Contact tank | 2 × 300 gallon
Filter Size | 2’(L)× 2’(W)× 17’(H) (Full size filter)
Filter Media | 6’ of Spent GAC or Anthracite
O₃/BAF pilot Specification

## Slide 54: Water Quality Through O₃/BAF Treatment
 | Secondary Treated Efflluent | Ozonated water/ Filter Inlet | BAF Outlet
COD | 21 – 33 mg/L | Not Measured | 10 - 20 mg/L
TOC | 4.8 – 7.0 mg/L | Not Measured | 3.0 - 5.5 mg/L
UVT | 58% – 72% | 65% - 82% | 70% - 89%
Turbidity | 7 – 10 NTU | Not Measured | 0.2 – 3.0 NTU
TSS | Not Measured | 5 – 10 mg/L | 0.2 – 2.4 mg/L
TKN | 2.8 mg/L | 2.1 mg/L | 1.4 mg/L
O3 dose = 0 – 15 ppm
Daily average values
Used GAC as filter media

## Slide 55: Impact of EBCT and O3 Dose on O3/BAF
Optimized Filter EBCT 12 min
Higher O3 dose, higher organic removal
Filter Media: Spent GAC

## Slide 56: Safety
See GAC and O₃ modules for information

## Slide 57: Critical Control Point Response Procedures
Critical Control Point Response Procedures
Critical monitoring and response procedures

## Slide 58: Ozone/BAC Alert Procedures

## Slide 59: Ozone/BAC Critical Failure Response Procedure

## Slide 60: Available Resources

## Slide 61
WaterRF Project # 4719: A Biofiltration Guidance Manual for Rapid-Rate Filtration Facilities

## Slide 62
The Water Research Foundation (WRF) is a nonprofit (501c3) organization which provides a unified source for One Water research and a strong presence in relationships with partner organizations, government and regulatory agencies, and Congress. The foundation conducts research in all areas of drinking water, wastewater, stormwater, and water reuse. The Water Research Foundation’s research portfolio is valued at over $700 million.
The Foundation plays an important role in the translation and dissemination of applied research, technology demonstration, and education, through creation of research-based educational tools and technology exchange opportunities. WRF serves as a leader and model for collaboration across the water industry and its materials are used to inform policymakers and the public on the science, economic value, and environmental benefits of using and recovering resources found in water, as well as the feasibility of implementing new technologies.
For more information, contact:
The Water Research Foundation
Alexandria, VA Office
1199 North Fairfax Street, Suite 900
Alexandria, VA 22314-1445
Tel: 571.384.2100
www.werf.org werf@werf.org
Denver, CO Office
6666 West Quincy Avenue
Denver, Colorado 80235-3098
Tel: 303.347.6100
www.waterrf.org Info@WaterRF.org
© Copyright 2018 by The Water Research Foundation. All rights reserved. Permission to copy must be obtained from The Water Research Foundation.
WRF ISBN: 978-1-60573-363-0
WRF Project Number: Reuse-15-05/4772
This report was prepared by the organization(s) named below as an account of work sponsored by The Water Research Foundation. Neither The Water Research Foundation, members of The Water Research Foundation, the organization(s) named below, nor any person acting on their behalf: (a) makes any warranty, express or implied, with respect to the use of any information, apparatus, method, or process disclosed in this report or that such use may not infringe on privately owned rights; or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of, any information, apparatus, method, or process disclosed in this report.
Hazen and Sawyer, Carollo Engineers Inc., Santa Clara Valley Water District
This document was reviewed by a panel of independent experts selected by The Water Research Foundation. Mention of trade names or commercial products or services does not constitute endorsement or recommendations for use. Similarly, omission of products or trade names indicates nothing concerning The Water Research Foundation's positions regarding product effectiveness or applicability.