## Slide 1: UV Disinfection and UV Advanced Oxidation Module

## Slide 2: Project Partners
Hazen and Sawyer
Carollo Engineers
Santa Clara Valley Water District
LA Sanitation District
Gwinnett County (GA)
El Paso Water Utilities
UFTREEO (University of Florida)
Sacramento State
University of Arizona-WEST Center
TrojanUV
Xylem Inc.
Process Applications Inc.
Calgon Carbon Corporation

## Slide 3: Acronyms
AOP | Advanced Oxidation Process
BAF | Biofiltration or Biologically Active Filtration
EEO | Electrical Energy per Order
ESB | Engineered Storage Buffer
HMI | Human Machine Interface
LP | Low Pressure UV Light
MF | Microfiltration
MP | Medium Pressure UV Light
NDMA | N-Nitrosodimethylamine
OH | Hydroxyl Radical
PDC | Power Distribution Center
RO | Reverse Osmosis
SCC | System Control Center
UF | Ultrafiltration
UV | Ultraviolet Light
UVI | Ultraviolet Light Intensity (Sensor Intensity)
UVT | Ultraviolet Light Transmittance

## Slide 4: Expected Learning Outcomes
How UV AOP fits into a potable reuse treatment train
Basic water quality considerations for UV AOP operation
Commonly used UV AOP terminology
How to calculate a UV Dose from online monitoring parameters
Most common control philosophies for UV AOP operation
Major system components and maintenance needs for UV AOP systems

## Slide 5: Role in Potable Reuse

## Slide 6: UV AOP Provides a Robust Barrier for a Final Treatment Process, by Providing Both Disinfection and Contaminant Removal
Disinfection (UV)
  Cryptosporidium
  Giardia
  Viruses
  Bacteria
Contaminant Removal (Photolysis and Oxidation)
  NDMA (N-nitrosodimethylamine) via photolysis
  Organic contaminants (i.e. pharmaceuticals, explosives, etc.) via photolysis and advanced oxidation with an oxidant addition
Regulatory Requirement for potable reuse

## Slide 7: In potable reuse systems, UV and UV AOP systems are placed at the end of an advanced treatment train to increase efficiency with the highest quality of water, and to provide the most robust pathogen barrier as the last defense before distribution
MF
ESB+Cl2
RO
UV/H2O2
Wastewater Treatment
UF
UV/H2O2
O3
ESB+Cl2
BAF
Wastewater Treatment

## Slide 8: UV Light for Disinfection and Chemical Photolysis

## Slide 9: UV Disinfection Works by Damaging the DNA of Microorganisms, Leaving Them Unable to Replicate and Infect
www.filterwater.com

## Slide 10: UV Photolysis Provides a Barrier for Contaminant Treatment, Such as NDMA Destruction
Trojan Technologies

## Slide 11: UV Disinfection Uses Low Wavelength UV to Provide a Higher Energy Output
UV Light is the portion of the electromagnetic spectrum where the wavelength is from 100 to 400 nanometers (nm)
The germicidal wavelength is 200nm to 300nm

## Slide 12: Lamp Wavelength Output Can be Narrow (Monochromatic) or Broad (Polychromatic) with Low Pressure vs. Medium Pressure UV
Source: Lenntech

## Slide 13: The Quantum Yield is Used as a Measure of Contaminant Destruction Efficiency
Photon (hν)
  Packet of energy as light at each λ
Einstein (Es)
1 mole of photons
Quantum Yield (Φ)
Efficiency of photochemical reaction moles of product per Einstein absorbed
6 x 1023 photons/mole
Product
Compound

## Slide 14: The Quantum Yield for a Contaminant is Not Easily Predictable
Can vary with wavelength
  Mono vs. polychromatic light considerations
Photons must be absorbed before transformation (1st law of photochemistry)
Unique to each contaminant
Ranges from <0.01 to >1

## Slide 15: Defining UV Dose Includes Both Energy and Time
Irradiance, mW/cm2 (E)
  Surface area normalized radiant power
UV Dose (Fluence), mJ/cm2 (E*time)
Surface area normalized radiant energy
Qin
Qout
Time

## Slide 16: UV is Effective for a Wide Variety of Pathogens, with Adenovirus Providing a Conservative Measure of UV Effectiveness

## Slide 17: Utilize Validated UV Reactors with Proven Disinfection Performance to Gain Necessary Pathogen Log Reduction Credits
Third Party Validated for
  UVT range (e.g., 90% to >95% UVT)
  Design flow range (project specific)
  Pathogen type (e.g., adenovirus) and log reduction target (e.g., 6-log)
Validations Require
  Large Flow Ranges (e.g., <1 mgd to >50 mgd)
  Large UVT Ranges (e.g., <55% UVT to >95% UVT)
  Seeded pathogen surrogates (e.g., MS2 coliphage)

## Slide 18: UV Advanced Oxidation Process (AOP)

## Slide 19: UV Advanced Oxidation Degrades Contaminants by Both Photolysis and Hydroxyl Radicals
Trojan Technologies

## Slide 20: UV Advanced Oxidant Processes (UV AOPs) Generate Highly Reactive •OH Species
•OH is a powerful, highly reactive and non-selective oxidant
•OH are short lived ~ 10µs
AOPs generate a very low steady-state concentration of •OH [10-12 to 10-13 M]
Need a high generation of •OH due to the short lifetime in the system
•OH do not need quenching post treatment

## Slide 21: UV/hydrogen Peroxide AOP and •OH Generation
Most commonly used AOP in water treatment is the UV/H2O2 process
Not heavily dependent on pH
Generation of •OH is based on the direct photolysis of H2O2:
Excess H2O2 will exist and may need quenching depending upon the end use
H2O2 + hn 2 •OH FOH = 1.0 mol/Es

## Slide 22: UV/hypochlorite AOP and •OH Generation
UV/hypochlorite AOP efficiency is dependent on chlorine speciation
  Chlorine species absorb UV light with varying efficiency across wavelengths
Excess chlorine residual will exist, quenching typically not necessary
Remucal and Manley, 2016

## Slide 23: UV/hypochlorite AOP is Heavily Dependent and Controlled by pH

## Slide 24: UV/hypochlorite Has the Highest Efficiency (Generates the Most •OH) at a Lower pH
Higher Quantum Yield

## Slide 25: •OH Has a High Relative Oxidant Power (E) Compared to Other Commonly Used Oxidants
Fluorine 2.23 V
Hydroxyl Radical (OH) 2.06 V
Atomic Oxygen (singlet) 1.78 V
Ozone 1.50 V
Hydrogen Peroxide 1.31 V
Perhydroxyl Radical (HO2) 1.25 V
Potassium Permanganate 1.24 V
Chlorine Dioxide 1.15 V
Bromine 0.80 V
Iodine 0.54 V

## Slide 26: Hydroxyl Radical Rate Constants
Units: KOH (M-1 s-1)
Not easily predictable
Affected by scavengers
Non-selective
Must be measured for each contaminant
Using competition kinetics
Rate constants for organic contaminants are typically >109 M-1 s-1
Linden Research Group

## Slide 27: Water Quality Considerations for UV AOP in Potable Water Reuse Treatment Trains
“High” Water Quality = “High” Process Efficiency
  Goal is to minimize the concentration of •OH “scavengers”
  Important WQ parameters
    UVT (UV Transmittance)
    Nitrogen species (chloramines, nitrite)
    pH (oxidant-dependent)
    Total organic carbon
    Alkalinity
Notes: Graph created with hypothetical data by Carollo, no citation needed.

## Slide 28: Case Study
Applied Contaminant Removal

## Slide 29: NDMA and Atrazine Removal Effectiveness by Low and Medium Pressure UV Photolysis
Contaminant | Low Pressure UV (LP) | Medium Pressure UV (MP)
NDMA | Effective | Effective
Atrazine | Not Effective | Effective

## Slide 30: NDMA Absorbs UV Light Across a Broad Range of Wavelengths
Both LP and MP emission overlap same absorbance band
Quantum yield constant below 280 nm (~ 0.3 mol/Es at pH 8)
Similar photolysis with LP and MP
Sharpless and Linden, Environ. Sci. Technol., 2003
N-nitrosodimethylamine

## Slide 31: Atrazine Absorbs UV Light Mostly at Low Wavelengths, Less than 254 nm
LP and MP lamps overlap different absorbance bands
Quantum yield differs above or below 250 nm (~ 0.03 vs 0.05 mol/Es)
Different results with LP and MP
Atrazine
For ATZ: MP >> LP
Sharpless et al., Aq. Sci., 2003
Notes: 2 bands at 265/370 and <250 nm the quantum yield is 0.05 ---different results as a result.

## Slide 32: NDMA and MIB Removal Using UV Photolysis and UV AOP
Contaminant | Percent Removal | Medium Pressure UV Dose Required (mJ/cm2)(a) | 
 |  | UV | UV/H2O2
NDMA | 90 | 550 | 570(b)
MIB | 90 | 5000 | 1000(c)
Measured as germicidal dose
100 ppm H2O2
7.5 ppm H2O2

## Slide 33: Oxidant Addition Provides No Additional Benefit to NDMA Destruction in the UV AOP
NDMA absorbs UV
Removal per photon is high (~ 0.3 mol/Es at pH 8)
H2O2 competes for photons
“Slow” reaction with OH (k = 3.3 x 108 M-1 s-1)
No benefit of H2O2
Sharpless and Linden, Environ. Sci. Technol., 2003

## Slide 34: Oxidant Addition is Necessary in the Destruction of MIB with a UV AOP
MIB absorbs UV poorly
H2O2 absorbs the light
Fast reaction with OH (k = 8.2 x 109 M-1 s-1)
Great benefit of H2O2
Rosenfeldt and Linden, JWSRT-Aqua., 2005

## Slide 35: A Comparison of Low and Medium Pressure UV Photolysis and Advanced Oxidation Processes to Potential Endocrine Disrupting Compounds (Edcs) Demonstrates Similar Performance for Lamp Types When Using AOP
BPA EE2 E2
Percent Destruction
100
80
60
40
20
0
LP
MP
15 ppm H2O2 + 1000mJ/cm2
LP
MP
>95% = BDL

## Slide 36: Control Philosophy

## Slide 37: Design Criteria for UV AOP Systems Use Online Monitoring Parameters for Alarms and Critical Setpoints to Maintain a UV Dose
UV Dose (minimum regulatory setpoint)
Power
Flow
UVT
UV Intensity (UVI)

## Slide 38: Power Input to the UV AOP System is Used to Maintain a UV Dose Setpoint

## Slide 39: As Flow Increases or Decreases, Power Will Increase or Decrease to Maintain a UV Dose Design Setpoint

## Slide 40: UV Transmittance is a Critical Parameter for Control and Operation of UV AOP Systems
Measured amount of UV light that can pass through a sample of water
Measured at a wavelength of 254 nm
Sample of water is measured and compared to distilled water
Trojan Technologies

## Slide 41: A decrease in UVT Will Correspond to a Decrease in the Applied UV Dose. More Power Will Need to be Applied to the System in Order to Maintain the UV Dose Design Setpoint

## Slide 42: UV Energy Efficiency is Dramatically Impacted by UV Transmittance (example data set not indicative of all systems)
Chart: Energy Use for Example UV Reactor for 50 mJ/cm2 @ 1 MGD
| 55 | 65 | 75 | 85 | 95
 | 18 | 10 | 4.4 | 2.2 | 0.8

## Slide 43: UV Reactor Efficiency is Impacted by Small UVT Changes in High Quality Water (example data set not indicative of all systems)
Chart: Sensitivity of UV Dose to UVT
| 95 | 96 | 97 | 98
 | 1 | 1.3 | 1.8 | 2.7

## Slide 44: UV Intensity (UVI) is Measured by Specialized Sensors, Placed Inside the UV Reactor, and is Used to Monitor the UV Light Output of Lamps
In the event of a lamp failure or decrease in lamp output, the UVI will respond by decreasing and will trigger an alarm if the target UV dose or target Power setpoint is not met

## Slide 45: A Decrease in UVI Will Correspond to a Decrease in the Applied UV Dose. More Power Will Need to be Applied to the System in Order to Maintain the UV Dose Design Setpoint.

## Slide 46: Design Criteria

## Slide 47: UV and UV AOP Provide Three Key Values for Potable Water Reuse Treatment
Pathogen Disinfection
  Giardia
  Cryptosporidium
  Virus
  Bacteria
Chemical Photolysis
  NDMA and other nitrosamines
Trace Chemical Advanced Oxidation
  Hormones
  Pharmaceuticals
  Personal Care Products
  0.5-log reduction of 1,4-dioxane is a common surrogate and regulated in CA

## Slide 48: UV and UV AOP Design Criteria Based Upon Treatment Process Decisions
Process Components | Notes | Pathogens | Regulated Pollutants | Unregulated CECs
O₃ | Advanced oxidation occurs here. | X | X | X
BAF |  |  | X | X
UF |  | X |  | 
GAC |  |  | X | X
UV | High dose UV system targeting 6-log reduction of all pathogens and 90% reduction in NDMA. Advanced oxidation not part of this process train. | X | X | X
Non-RO Purification Train Example

## Slide 49: UV and UV AOP Design Criteria Based Upon Treatment Process Decisions
Process Components | Notes | Pathogens | Regulated Pollutants | Unregulated CECs
MF/UF |  | X |  | 
RO |  | X | X | X
UV AOP | High dose UV system targeting 6-log reduction of all pathogens and 90% reduction in NDMA Advanced oxidation is included here, through addition of either hydrogen peroxide or sodium hypochlorite | X | X | X
RO Purification Train Example

## Slide 50: Water Quality for UV/UV AOP Without RO
O3/BAF/UF/GAC Pretreatment
O₃, BAF, and GAC all raise UVT. Typical value is 90% to 93% UVT after GAC
O₃/BAF (combined) and GAC each reduces TOC. Typical value is 2.5 to 3.5 mg/L after GAC
BAF and UF lower turbidity. Typical value post UV is <0.1 NTU
pH is stable following BAF Treatment, in the 7 to 8 range
There will likely be more hydroxyl radical scavengers in the feed to UV for UV advanced oxidation, potentially making it less effective
Note: The O₃ process is effective for advanced oxidation, so UV AOP may be unnecessary

## Slide 51: Water Quality for UV/UV AOP With RO
MF/RO Pretreatment
RO will raise UVT. Typical value is >95%, can be >99% with new RO membranes
TOC post RO is <0.3 mg/L
Turbidity post RO is <0.1 NTU
pH post RO is not stable (no alkalinity) and is in the 6.0 to 6.5 range.
There are few hydroxyl radical scavengers in the feed to UV for UV advanced oxidation. These potentially include chloramines.
Low pH of the feed water makes UV/NaOCl effective
UV/H2O2 also effective, independent of pH

## Slide 52: Utilize Validated UV Reactors and Set the Dose Based Upon Pathogen Disinfection Targets

## Slide 53: Control Philosophies for Disinfection and Advanced Oxidation
EEO
UV Dose and Oxidant Weighted Dose
UV/chlorine and pH

## Slide 54: EEO Approach
Electrical Energy Per Order (EEO)
Used for UV AOP system sizing and operation
Focused on chemical destruction (not disinfection credit)
Conservative estimations
Limited use of sensors
Not a preferred approach for new systems
Radicals Destroy
Contaminants
Water
UV Light
UV + Peroxide
 OH Radicals
Peroxide

## Slide 55: Calculate the Number of Reactors Needed to Remove 2 Log of a Contaminant at a Flow of 1 Mgd Based on a System Design of 18 Lamps Per Reactor and 20 kW/lamp
Units = kW-hr per 1000 US gallons
  Target Contaminant Reduction = 2 log
  Flow = 1 mgd
  EEO = 10 kW-hr per 1000 US gallon per log reduction
  Therefore Required Power = 833 kW
  UV System:
  3 reactors
  18 lamps per reactor
  20 kW per lamp

## Slide 56: Other Dosing and Control Systems Can Improve “Real-time” Dose Monitoring (UV/H2O2 Example) by Utilizing Both the Oxidant Dose and the UV Dose with Real Time Monitoring
City of Oxnard, CA
UV Intensity
Flow
Oxidant Dose
Notes: Highlights on this slide:
Control algorithms are typically focused on UV Dose alone, this incorporates the UV and oxidant dose, verified in real time by the UV sensor intensity.
An example of a UV/peroxide system operating with this control strategy

## Slide 57: Other Dosing and Control Systems Can Improve “Real-Time” Dose Monitoring (UV/NaOCl example) Utilizing the Oxidant UV Dose, and pH
City of Los Angeles, CA
UV Intensity
UVT
Flow
Oxidant Dose
Notes: Highlights on this slide:
Control algorithms are typically focused on UV Dose alone, this incorporates the UV and oxidant dose, verified in real time by the UV sensor intensity.
Example of a potential control algorithm that utilizes the possibility of pH control/adjustments.
An example of a UV/hypochlorite system operating with this control strategy.

## Slide 58: UV AOP Chemistry is Complex… and Still Not Fully Defined
C = Contaminant concentration
C0 = Initial contaminant concentration
DCont = Contaminant weighted UV Dose (mJ/cm2)
DH2O2 = Peroxide weighted UV Dose (mJ/cm2)
k’d = Pseudo 1st Order Kinetic constant for photolysis (cm2/ mJ)
k’OH = Pseudo 1st Order Kinetic constant for advanced oxidation (cm2/ mJ)
 = Wavelength (nm)
kx = Second order rate constant for reactor of water quality parameter “x” with the hydroxyl radical (L/mol-s)
h = Planck’s constant (m2-kg/s)
C = Speed of light (m/s)
NA = Avogadro’s number
 = Quantum efficiency of hydroxyl radical formation
 = Molar extinction coefficient of hydrogen peroxide (L/mol-cm)
Number of •OH radicals produced
Number of •OH radicals scavenged by water quality parameters

## Slide 59: The Efficiency of a UV/chlorine AOP is Dependent on pH Due to Chlorine Speciation, Molar Absorptivity, and •OH Generation
Low Pressure UV
RO Permeate

## Slide 60: pH Monitoring and/or Control is Important for Ensuring a UV/Chlorine AOP is Meeting Design Conditions, as the Lower the Ph, the More Efficient the AOP
pH
•OH generation (efficiency)

## Slide 61: Example of Increased Efficiency for Atrazine Removal at a Lower pH Using a UV/Chlorine AOP
Kong et. al. (2016) Water Research
Atrazine
UV Only
pH 9
pH 7
pH 5

## Slide 62: Process Alarms and Response

## Slide 63: Setting and Responding to Alarms (Critical)
UV Dose
  EEO
  Oxidant Weighted Dose
  Other
Flow Signal
Concept | Value
Dose Set-point is 10% above regulated target | Allows for variability of real-time input from UVI, UVT, and Q
Operational Capacity is 125% above necessary capacity | Allows time for standby or redundant equipment to come online and warm up
Correlate Dose to Pathogen Log Reduction | Allows continued operation in event of low dose if total process log reduction acceptable
Flow signal failure results in instant diversion | Necessary for dose control

## Slide 64: Setting and Responding to Alarms (Non-Critical)
UV Intensity (UVI)
UV Transmittance (UVT)
Concept | Value
Correlate UV and Oxidant Dose to Chemical Destruction | Diversion only necessary for acute risk items, not chronic chemical issues
Trend UVT and UVI Proactive maintenance and calibration | Diversion only needed if dose is not met and pathogen log reduction goals for treatment train not met

## Slide 65: Human Machine Interface (HMI) Examples
Local = Lamps ON @ 100% power
Remote = Lamp operation controlled by SCC
OFF = Lamps OFF Locally
Selector Switch
UV Zone Display
Upper Display indicates UV Sensor value in mW/cm2
Middle Display indicates system status
0, 60 – 100 Value = Power Level of Module
LO OP = Controller in Local Mode of Operation
PAUSE = System in Remote & Lamps are OFF
Lower Display indicates # of lamps & flashes lamp # for lamp faults

## Slide 66: Example Alarm Types for a Trojan UV Reactor
Alarm Types
Lamp Failure
Zero Offset Error
System Needs Cleaning
Prox Failure
Home Not Found
Low Flow
Lamp Needs Replacing

## Slide 67: Human Machine Interface (HMI) Examples
Press to perform desired control function
Action Buttons
Status Display
Provides system operational information
Navigation Buttons
Press to view the desired system information
Sub Section Buttons
Press to view/control subsystem information
Alarms Banner
Displays system alarms
Note: Refer to O&M Manual for detailed information

## Slide 68: Data Trending and Response
Calibrated UV sensors measure UVI
Clean sleeve UVI benchmarks allow for sleeve fouling analysis
Proactive cleaning allows for controlled sleeve fouling and a balance between energy efficiency and operations and maintenance efforts.
Altamonte Springs, FL
Clean Sleeves Here

## Slide 69: Process Components

## Slide 70: Major Components of a UV System
UV Reactor
Chamber
PDC
(Power
Distribution
Center)
SCC
(System Control Center with Human Manchine Interface (HMI))
UV Train (2 shown)

## Slide 71: Major Process Components of a UV System
Inlet Flange
Support Frame
Air Vacuum
Valve
Level Switch
Temperature
Sensor
UV Intensity
Sensor
Service
End Cap
Outlet
Flange
Chamber
Mounting
Bracket
UV Reactor
Chamber

## Slide 72: Chamber End Plate
Sleeve Bolts
UV Intensity
Sensor
Connector
Lamps
Water
Temperature
Sensor
Connector
Temperature
Switch
Service
End Cap
Latch (4)
Safety Cover
Switch
Conduits
To PDC

## Slide 73: UV Lamp & Sleeve
Lamp Plug
Lamp Plug
Retaining Nut
Sleeve Bolt
End
Plate
Lamp Plug
Washer
Sleeve O-Ring
Lamp
Sleeve
Sleeve Holder
Bushing
Spring
Stop Plate

## Slide 74: Major Components of UV System
Level Switch
Detects water level in UV Unit
Provides discrete output signal to controls system to indicate Unit full condition
Temperature Sensor
Measure water temperature Leaving the UV Train
Provides 4-20 mA signal to controls system to indicate actual water temperature
LCD displays Water Temp.

## Slide 75: Major System Components
End Cap Switch
Detects when the End Cap is removed
Provides discrete output signal to the controls system to shut off power to the ballast/lamps
Temperature Switch
Detect temperature on the end plate of the Reactor Chamber
Provides discrete signal to controls system to indicate if the UV Unit temperature is above 50C (122F)

## Slide 76: Power Distribution Center (PDC)
Local – Off - Remote
Selector Switch
Inlet Filter
Module Display –
Communication
Control Board
PDC Main
Disconnect Handle
Exhaust
Fan
Door Handle

## Slide 77: PDC System Controls
Temperature
Switches
Main
Power
Disconnect
Conduits to
Reactor
Communication
Board
Lamp Wire
Terminal
Blocks
Ballast’s
Control
Devices &
Relays
Circuit Breakers
& Fuses

## Slide 78: System Control Center (SCC)
Provides overall control of the PDC / UV Trains and other associated equipment
Provides operator interface for system status, alarms, and control
Coordinates communication to PDCs, UVRs, Flowmeters, OptiView, Valves, Pumps, and Plant SCADA system
Door
Handle
Operator
Interface

## Slide 79: Major Wear Items and Proper Disposal
Wear Item | Lifetime | Disposal
UV Lamp | 5,000 hours to 15,000 hours | Contains mercury. Recycle back to Supplier
Ballasts | Typically 5 years | Recycle back to Supplier
Wipers | Typically 6 months to 3 years for some components | Landfill wiper rings. Other components can be reused.
Quartz sleeves | 5 to 10 years for medium pressure UV systems 5 to 20 years for low pressure UV systems | Landfill

## Slide 80: Critical Control Point Response Procedures

## Slide 81: Critical Control Point Response Procedures
The following critical control point response procedures are taken from WRF project Reuse-13-03. They are generic in nature and are provided as a guide. Examples for these response procedures are provided in the Supporting Information slides in this module.

## Slide 82: Operation and Maintenance

## Slide 83: System Monitoring and Performance Verification
Parameter | Frequency | Calibration
UV Dose | Real Time | No calibration
UV Intensity | Real Time | ~Monthly
UV Transmittance | Real Time | Daily
Flow | Real Time | At Startup, and ideally annually based upon parallel flow meters
Microbiological | Grab Sample, Daily | No calibration
Oxidant Feed | Daily or Weekly | Pump drawdown verification

## Slide 84: Example Lamp Replacement on One Type of UV Reactor; Each UV Reactor Will Come with a Detailed O&M Manual
Remove the Service End Cap
Unscrew Lamp Holder Nut from the Sleeve Bolt
Pull Lamp Holder from Sleeve Bolt to access Lamp
Disconnect Lamp Holder from the Lamp & remove Lamp
1.
2.
3.
4.

## Slide 85: Example Lamp Installation on a Trojan UV Reactor
Slide Lamp into Sleeve
Align Lamp and Lamp Holder Index ledges and connect Lamp Plug onto Lamp
Push Lamp Holder into Sleeve Bolt until Holder stop touches Sleeve Bolt
Slide Washer and Lamp Holder Nut onto Bolt and Hand tighten
Install Service End Cap
1 & 2.
3.
4.
4.
5.

## Slide 86: Example Sleeve Removal on a Trojan UV Reactor
Position Sleeve Bolt Tool over Sleeve Bolt and unscrew from End Plate
Insert Sleeve Removal Tool into the Sleeve
Pull firmly on the ball end of the removal tool
Pull the Sleeve straight out from the End Plate
Remove and inspect the Sleeve Sealing O-ring
1.
2.
3 & 4.
5.

## Slide 87: Example Sleeve Replacement on a Trojan UV Reactor
Insert the Sleeve Sealing O-ring into the seat in the end plate
Moisten the Sleeve and Insert into the End plate
Slide Sleeve straight into the Reactor Chamber ensuring the end of the Sleeve goes into the support bushing on the stop plate
Install Sleeve Bolt by hand and tighten with the Sleeve Bolt Tool
Tighten the Sleeve Bolt to 60 in – lbs using the Sleeve Bolt Tool
1.
2 & 3.
4.
5.

## Slide 88: Example UV Sensor Cleaning and Calibration for Trojan UV Reactor
Knurled
Nut
UVSensor
Optical Window
Removable
Sensor
Window
UV Sensor
Plug
UV Sensor
Assembly

## Slide 89: Example UV Sensor Cleaning and Calibration for Trojan UV Reactor
Disconnect the UV Sensor Cable from the UV Sensor Assembly
Unscrew UV Sensor Knurled Nut and pull Sensor from Window
Unscrew the Sensor Window from the Reactor Chamber
Clean optical window and removable window with cotton swab and cleaning solution
Reinstall and Tighten Sensor Window to 40 in-lbs and UV Sensor hand tight
1.
2.
3.
4.

## Slide 90: Example UV Ballast Removal for Trojan UV Reactor
Disconnect Ballast power connector
Release the comm. cable connector clips and remove the cable and the ground strap
Remove the mounting screw and slide the ballast out from the rear mounting clip
Disconnect the 2 lamp cable connectors at the rear of the ballast
Ballast Power
Connector
Ballast
Communication
Connector
Ballast
Mounting
Clip
Ballast
Lamp
Connectors
1 & 2.
3.
4.

## Slide 91: Example UV Ballast Installation for Trojan UV Reactor
Set Ballast address on dipswitch to match previous Ballast setting
Connect the 2 lamp connectors at the rear of the ballast
Slide the ballast into the rear mounting clip and install mounting screw
Push the comm. cable connector into the socket and close clips
Connect the ground strap and the Ballast power cable connector
Ballast Dipswitch
1.
2.
3.
3 & 4.

## Slide 92: Safety

## Slide 93: Hazards Overview
UV Light Hazard
  Use protective face shield & clothing
Electrical Hazards
  Follow Lock-out Tag-out procedures!
Mechanical Hazards
  Fluid Pressure

## Slide 94: Supporting Information

## Slide 95: UV Disinfection Alert Response Procedure

## Slide 96: UV Disinfection Critical Response Procedure

## Slide 97: UV Advanced Oxidation Alert Response Procedure

## Slide 98: UV Advanced Oxidation – Critical Response

## Slide 99
The Water Research Foundation (WRF) is a nonprofit (501c3) organization which provides a unified source for One Water research and a strong presence in relationships with partner organizations, government and regulatory agencies, and Congress. The foundation conducts research in all areas of drinking water, wastewater, stormwater, and water reuse. The Water Research Foundation’s research portfolio is valued at over $700 million.
The Foundation plays an important role in the translation and dissemination of applied research, technology demonstration, and education, through creation of research-based educational tools and technology exchange opportunities. WRF serves as a leader and model for collaboration across the water industry and its materials are used to inform policymakers and the public on the science, economic value, and environmental benefits of using and recovering resources found in water, as well as the feasibility of implementing new technologies.
For more information, contact:
The Water Research Foundation
Alexandria, VA Office
1199 North Fairfax Street, Suite 900
Alexandria, VA 22314-1445
Tel: 571.384.2100
www.werf.org werf@werf.org
Denver, CO Office
6666 West Quincy Avenue
Denver, Colorado 80235-3098
Tel: 303.347.6100
www.waterrf.org Info@WaterRF.org
© Copyright 2018 by The Water Research Foundation. All rights reserved. Permission to copy must be obtained from The Water Research Foundation.
WRF ISBN: 978-1-60573-363-0
WRF Project Number: Reuse-15-05/4772
This report was prepared by the organization(s) named below as an account of work sponsored by The Water Research Foundation. Neither The Water Research Foundation, members of The Water Research Foundation, the organization(s) named below, nor any person acting on their behalf: (a) makes any warranty, express or implied, with respect to the use of any information, apparatus, method, or process disclosed in this report or that such use may not infringe on privately owned rights; or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of, any information, apparatus, method, or process disclosed in this report.
Hazen and Sawyer, Carollo Engineers Inc., Santa Clara Valley Water District
This document was reviewed by a panel of independent experts selected by The Water Research Foundation. Mention of trade names or commercial products or services does not constitute endorsement or recommendations for use. Similarly, omission of products or trade names indicates nothing concerning The Water Research Foundation's positions regarding product effectiveness or applicability.